Part 2

Component Layout and

Refrigerant Circuits

1 Layout of Functional Components	6

2 Piping Diagrams	8

Layout of Functional Components

Piping Diagrams

Refrigerant piping graphic example:

High-temperature, high-pressure gas
High-temperature, high-pressure liquid

Low-temperature, low-pressure gas liquid mixture

Low-temperature, low-pressure gas

Medium-temperature, medium-pressure gas

Note: Direction of refrigerant flow depicted in diagram represents main refrigerant flow and is for illustration purposes only.

Heating mode (EVI off)

Cooling mode (EVI off)

Heating mode (EVI on)

Cooling mode (EVI on)

Key components

| Legend |  |  |
| --- | --- | --- |
| No. | Symbol | Description |
|  | COMP | DC inverter compressor |
|  | HEAT3 | Crankcase heater |
|  | Tp | Discharge temperature sensor |
|  | HP | High-pressure switch |
|  | HS | High-pressure sensor |
|  | ST1 | 4-way valve |
|  | / | Pin valve (discharge side) |
|  | FAN A / B | DC fan A / DC fan B |
|  | / | Finned tube Heat exchanger |
|  | T4 | Ambient temperature sensor |
|  | T3 | Outdoor unit heat exchanger bottom temperature sensor |
|  | TL | Outdoor unit heat exchanger outlet temperature sensor |
|  | / | Filter |
|  | EEV1 | Heating electronic expansion valve |
|  | / | One-way valve |
|  | EEV3 | EVI electronic expansion valve |
|  | / | Plate heat exchanger (economizer) |
|  | T9I | Economizer inlet temperature sensor |
|  | T9O | Economizer outlet temperature sensor |
|  | / | Gas-liquid separator |
|  | Th | Compressor suction temperature sensor |
|  | LS | Low-pressure sensor |
|  | EEV2 | Cooling electronic expansion valve |
|  | / | One-way valve |
|  | / | Accumulator tank |
|  | T2 | Plate heat exchanger temperature sensor |
|  | T2B | Plate heat exchanger temperature sensor |
|  | / | Plate heat exchanger |
|  | / | Plate heat exchanger heat tape |
|  | TW_in | Inlet water temperature sensor |
|  | TW_out | Outlet water temperature sensor |
|  | / | Water pump |
|  | / | Expansion vessel |
|  | / | Automatic air vent valve |
|  | FS | Water flow switch |
|  | / | Automatic air vent valve |
|  | / | Safety valve |

- Compressor

The refrigerant is compressed which also raise its temperature. The refrigerant enters the compressor as a low-pressure, low-temperature gas and exits the compressor as a high-pressure, high-temperature gas.

- 4-way valve

To better control refrigerant flow, Mars series features an upgraded 4-way valve default position which remains closed in heating mode (no electrical signal) and open in cooling mode. When closed, the air-side heat exchanger functions as an evaporator and water side heat exchanger functions as a condenser; when open, the air side heat exchanger functions as a condenser and water side heat exchanger function as an evaporator.

- High-pressure switch

A high-pressure switch regulates system pressure by shutting off the compressor in the event the refrigerant-system pressure exceeds the upper limit.

- Air side heat exchanger (Finned tube heat exchanger)

Heat is transferred from the refrigerant into the surrounding air by first passing through the tube coils where the heat is transferred to the fins via conduction. It then dissipates into the air forced through the heat exchanger.

- Filter

An air filter traps incoming dust, pet dander, fibers and other airborne contaminants, helping to protect interior heat pump components.

- Electronic expansion valve (EXV)

Controls refrigerant flow and reduces refrigerant pressure as necessary.

- Accumulator tank

Stores excess fluid refrigerant during system operation.

- Plate heat exchanger

Facilitates transfer of heat between two fluids. This type of exchange offers a significant advantage over conventional heat exchangers as fluids are exposed to a much larger surface area which better facilitates the transfer of heat while greatly accelerating temperature increase.

- Water pump (Circulating pump)

Circulates water throughout the water circuit.

- Automatic air purge valve

Automatically removes air from the water circuit.

- Water flow switch

Monitors the flow rate of water to detect insufficient flow, preventing potential damage.