Part 3

Control and Field settings

1 Shut-off Operation	15

2 Standby Control	15

3 Startup Control	16

4 Normal Operation Control	19

5 System protection features	21

6 Other Controls	26

7 User Interface Field Settings	27

8 USB Function Field Settings	59

- Refer to system diagram below for location of key components and sensors.

- The diagram below is for reference only. Actual installations will vary based on unique system configurations.

Notice

Shut-off Operation

The unit will automatically shut off if one of the following occurs:

- System abnormality: to protect the compressor, a thermal sensor will automatically shut the system off if it detects any abnormality that could potentially cause damage. An error code will show on both the outdoor unit PCB digital display and the user interface.

- Set temperature has been reached: system will shut off

Standby Control

Crankcase Heater Control

A crankcase heater is used to prevent refrigerant from mixing with compressor oil during compressor shutdown. The crankcase heater operation is determined by outdoor ambient temperature and whether the compressor is on or off. When outdoor ambient temperature is above 10°C or the compressor is running, the crankcase heater is off. When outdoor ambient temperature is at or below 8°C and the compressor has either been off for more than 3 hours or the unit has recently been powered on (either manually or following a power outage), the crankcase heater will activate.

Water Pump Control

- HMI set “Water temperature” control type: If heating or cooling mode =ON, When unit in standby state, the internal and external circulator pumps keep running continuously.

- HMI set “Room temperature” control type: If heating or cooling mode =ON, When unit in standby state, the internal and external circulator pumps will stop running.

- HMI set “Water temperature” control type and “Tbt=YES”: If heating or cooling mode =ON, When unit in standby state, the internal circulator pump will stop running and external circulator pumps keep running continuously.

Startup Control

Compressor Startup Delay Control

Startup control and restart control delay compressor startup by three minutes from the last stoppage in order to prevent the potentially harmful effects of frequent compressor on/off cycling and also ensures that pressure within the refrigerant system remains equalized. (Note: this feature will not affect oil return or defrosting operation)

Unit Startup

In initial startup or restart control, compressor startup is determined by outdoor ambient temperature and parameters input into one of two startup programs in order to reach the target rotation speed.

Cooling start mode 1 Compressor startup program when cooling mode ambient temperature is above 12°C

20 S

Cooling start mode 2 Compressor startup program when cooling mode ambient temperature is below 12°C

20 S

Note: Preset running mode 1 and Preset running mode 2 are the two frequencies at which the compressor operates

Component control during startup in cooling mode

| Component | Wiring diagram label | 26-40 kW | Control functions and status |
| --- | --- | --- | --- |
| Inverter compressor | COMP | ● | Compressor startup program selected according to ambient temperature1 |
| DC fan motor | FAN | ● | Fan run at maximum speed2 |
| Electronic expansion valve | EEV2 | ● | Increments from 0 (fully closed) to 480 (fully open), controlled according to outdoor ambient temperature, discharge temperature, suction superheat, compressor speed and refrigerant system pressure |
| Four-way valve | 4-WAY | ● | ON |
| Notes: - Refer to “Startup Control - Unit Startup”. - Refer to “Normal Operation Control - Outdoor Fan Control” |  |  |  |

Heating start mode 1 Compressor startup program when heating mode ambient temperature is above 0°C 20 S Heating start mode 2 Compressor startup program when heating mode ambient temperature is below 0°C 20 S Heating start mode 3 Compressor startup program when heating mode ambient temperature is below -20°C and discharge temperature is below 5°C 150 S 20 S

Note: Preset running mode 1 and Preset running mode 2 are the two frequencies at which the compressor operates

Component control during startup in heating and domestic hot water modes

| Component | Wiring diagram label | 26-40 kW | Control functions and status |
| --- | --- | --- | --- |
| Inverter compressor | COMP | ● | Compressor startup program selected according to ambient temperature1 |
| DC fan motor | FAN | ● | Fan runs at maximum speed2 |
| Electronic expansion valve | EEV1 | ● | Increments from 0 (fully closed) to 480 (fully open), controlled according to outdoor ambient temperature, discharge temperature, suction superheat, compressor speed and refrigerant system pressure |
| Four-way valve | 4-WAY | ● | OFF |
| Notes: - Refer to “Startup Control -Unit Startup”. - Refer to “Normal Operation Control - Outdoor Fan Control” |  |  |  |

Normal Operation Control

Component Control during Normal Operation

Component control during heating and domestic hot water (DHW) operations

| Component | Wiring diagram label | 26-40 kW | Control functions and status |
| --- | --- | --- | --- |
| Inverter compressor | COMP | ● | Controlled according to load requirement determined by temperature and outdoor water temperature settings. |
| DC fan motor | FAN | ● | Controlled according to outdoor heat exchanger pipe temperature |
| Electronic expansion valve | EEV1 | ● | Increments from 0 (fully closed) to 480 (fully open), controlled according to outdoor ambient temperature, discharge temperature, suction superheat, compressor speed , refrigerant system pressure and temperature |
| Four-way valve | 4-WAY | ● | OFF |

Component control during cooling operation

| Component | Wiring diagram label | 26-40 kW | Control functions and status |
| --- | --- | --- | --- |
| Inverter compressor | COMP | ● | Controlled according to load requirement determined by temperature and outdoor water temperature settings. |
| DC fan motor | FAN | ● | Controlled according to outdoor heat exchanger pipe temperature |
| Electronic expansion valve | EEV2 | ● | Increments from 0 (fully closed) to 480 (fully open), controlled according to outdoor ambient temperature, discharge temperature, suction superheat, compressor speed and refrigerant system pressure |
| Four-way valve | 4-WAY | ● | ON |

Compressor Output Control

The compressor rotation speed is influenced by the load requirement. Before compressor startup, the outdoor unit calculates the target speed based on the outdoor ambient temperature, set leaving water temperature, and actual leaving water temperature.  It then runs the appropriate compressor startup program. (Refer to Part 3.2 “Compressor Startup Program”). After completion of the startup program, the compressor operates at the specified rotation speed.  During operation, compressor speed is modulated based rate of water temperature change, refrigerant system pressure and the refrigerant temperature.

Compressor Frequency Control

The running speed of a four-pole compressor, measured in rotations per second (rps), is one third of the electrical input frequency in hertz (Hz) to the motor. The frequency of the electrical input to the compressor can be altered at a rate of 1Hz per second.

Four-way Valve Control

A four-way valve is employed to change the direction of the refrigerant flow through the water-side heat exchanger which enables switching between cooling and heating/DHW operations. The valve is open during cooling but closed during heating and DHW production.

Electronic Expansion Valve Control

Heating / Cooling electronic expansion valve (EEV1/EEV2)

The electronic expansion valve (EEV) is controlled in increments from 0 (fully closed) to 480 (fully open).

- At power-on:

  - The EEV first closes fully, then moves to the standby at the 480 increments position. After the compressor activates, the EEV control is determined by suction superheat discharge temperature, pressure, discharge temperature and compressor speed.

- When the outdoor unit is in standby mode:

  - The EEV is at the 480 increment.

- When the outdoor unit shut offs:

  - The EEV first moves to the 480 increment where it remains for 30 seconds. It then closes fully before moving to the standby position at the 480 increment.

EVI electronic expansion valve (EEV3)

The EVI electronic expansion valve is a control valve that controls the middle air supply of the compressor.

EEV3 controls the opening of the outlet superheat through the ECO board. EEV3 controls the outlet superheat between 2 °C and 5 °C. Efficient and reliable control through Proportion Integration Differentiation (PID) control. Determine that the compressor frequency is greater than 56 Hz and the exhaust superheat is greater than 15 °C, open the EEV3 valve. Close the EEV3, when the compressor frequency is low or the exhaust superheat is low.

Outdoor Fan Control

The outdoor unit fan speed can be adjusted in a series of incremental steps as shown below.

| Fan speed control during operation |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Fan speed index | Upper Fan speed (rpm) | Lower Fan speed (rpm) | Fan speed index | Upper Fan speed (rpm) | Lower Fan speed (rpm) |
| W0 | 0 | 0 | W17 | 460 | 460 |
| W1 | 130 | 0 | W18 | 490 | 490 |
| W2 | 160 | 0 | W19 | 520 | 520 |
| W3 | 180 | 0 | W20 | 550 | 550 |
| W4 | 200 | 0 | W21 | 580 | 580 |
| W5 | 230 | 0 | W22 | 610 | 610 |
| W6 | 130 | 130 | W23 | 640 | 640 |
| W7 | 170 | 170 | W24 | 670 | 670 |
| W8 | 190 | 190 | W25 | 700 | 700 |
| W9 | 220 | 220 | W26 | 730 | 730 |
| W10 | 250 | 250 | W27 | 760 | 760 |
| W11 | 280 | 280 | W28 | 790 | 790 |
| W12 | 310 | 310 | W29 | 810 | 810 |
| W13 | 340 | 340 | W30 | 850 | 850 |
| W14 | 370 | 370 | W31 | 880 | 880 |
| W15 | 400 | 400 | W32 | 920 | 920 |
| W16 | 430 | 430 | / | / | / |

System protection features

High Pressure Protection

This feature protects the refrigerant system from abnormally high pressure and also protects the compressor from transient spikes in pressure.

Pc > 3.5MPa Pc < 2.6MPa Normal operation High pressure protection, error code P1 is displayed

Notes: - Pc: Discharge pressure

When the discharge pressure rises above 3.5MPa the system displays the error code P1 and the unit shuts down. When the discharge pressure drops below 2.6MPa, the compressor restarts.

Low Pressure Protection

This feature protects the refrigerant system from abnormally low pressure and also protects the compressor from transient drops in pressure.

Pe < 0.13MPa Pe ≥0.20MPa Normal operation Low pressure protection, error code P0 is displayed

Notes: - Pe: Suction pressure

When the suction pressure drops below 0.13MPa the system displays the error code P0 and the unit shuts down. When the suction pressure rises above 0.2MPa, the compressor restart.

Discharge Temperature Protection

This control protects the compressor from abnormally high temperatures and transient spikes in temperature.

High discharge temperature protection control

Discharge temperature > 115°C Discharge temperature < 95°C Normal operation High discharge temperature protection, error code P4 is displayed

When the discharge temperature rises above 115°C the system displays the error code P4 and the unit shuts down. When the discharge temperature drops below 95°C, the compressor enters re-start mode.

Low discharge temperature protection control

Compressor running time≥ 12min， and Tp<-20℃(or Tp<Th lasts 30s) After 3 minutes Normal operation Low discharge temperature protection, error code EA is displayed

When the discharge temperature (Tp) is below suction temperature (Th) for more than 12 minutes after compressor operates, the system displays the error code EA and the unit shuts down. After 3 minutes the compressor enters re-start control.

Note: EA protection occurs 3 times within 2 hours, the outdoor unit cannot be restarted unless it is powered on again.

Compressor Current Protection

This control protects the compressor from abnormally high currents.

Current > Currentmax Current < Currentmax Normal operation Compressor current protection, error code P3 is displayed

| Model |  | 26-40 kW |
| --- | --- | --- |
| Currentmax | Cool mode | 33 A |
|  | Heat or DHW mode | 35 A |

When the compressor current rises above Currentmax the system displays the error code P3 and the unit shuts down. When the compressor current drops below Currentmax, the compressor enters re-start mode.

Voltage Protection

This protects the M-Thermal Split from abnormally high or abnormally low voltages.

Voltage ≥ 265V or Voltage ≤ 172V 180V≤Voltage < 256V for 30s Normal operation Compressor voltage protection, error code H7 is displayed

When the phase voltage of AC power supply is at or above 265V, the system displays the error code H7 and the unit shuts down. When the phase voltage drops below 265V for more than 30 seconds, the refrigerant system restarts once the compressor re-start delay has elapsed. When the phase voltage is below 172V, the system displays the error code H7 and the unit shuts down. When the AC voltage rises to more than 180V, the refrigerant system restarts once the compressor re-start delay has elapsed.

DC Fan Motor Protection

This control protects the DC fan motors from strong winds and abnormal power supply. DC fan motor protection occurs when any one of the following conditions are met:

- Fan speed continues to be less than 50rpm more than 40S from the set fan step＞0

- Fan speed is lower than 50rpm for 3S,during normal operation

When DC fan motor protection control occurs the system displays the H6 error code and the unit shuts down. After 30S, the unit restarts automatically. When H6 protection occurs 10 times in 120 minutes, the HH error is displayed. When an HH error occurs, a manual system restart is required before the system can resume operation.

Anti-freezing Protection

This control protects the water-side heat exchanger from ice formation. The water-side heat exchanger electric heater is controlled according to outdoor ambient temperature, water-side heat exchanger water inlet temperature and water-side heat exchanger water outlet temperature.

In cooling mode, if inlet water temperature or leaving water temperature or auxiliary heat source leaving water temperature is below 4°C, the anti-freeze protection actions. In heating/DHW mode, if ambient temperature is below 3°C and inlet water temperature or leaving water temperature or auxiliary heat source leaving water temperature is below 4°C, the anti-freeze protection actions. In heating/DHW mode, leaving water temperature is below 2°C, the anti-freeze protection actions.

When water-side heat exchanger anti-freeze protection occurs the system displays error code Pb and the unit shuts down. .

Note: For the clear and concise understanding of anti-freeze protection, the diagram is illustrated as below.

Anti-freezing control in Cooling mode

Tw_out: Plate heat exchanger outlet water temperature Tw_in: Plate heat exchanger inlet water temperature T1: Electric Heater/AHS water outlet temperature

Anti-freezing control in Off status/ Heating mode/ DHW mode

T4: Ambient temperature Tw_out: Plate heat exchanger outlet water temperature Tw_in: Plate heat exchanger inlet water temperature T1: Electric Heater/AHS water outlet temperature T1STOPH: The maximum temperature to stop compressor in heating mode

Other Controls

Defrosting Function

In order to recover heating capacity, defrosting occurs when air-side heat exchanger of the outdoor unit acts as a condenser. Defrosting is automatically controlled based on the outdoor ambient temperature, the outlet temperature of the air-side heat exchanger refrigerant and the compressor run time.

Component control during defrosting operation

| Component | Wiring diagram label | 26-40 kW | Control functions and status |
| --- | --- | --- | --- |
| Inverter compressor | COMP | ● | Runs at defrosting operation rotation speed |
| DC fan motor | FAN | ● | Off |
| Electronic expansion valve | EEV1 | ● | Fully open |
| Four-way valve | 4-WAY | ● | ON |

User Interface Field Settings

Introduction

During installation, the installer determines settings based on configuration parameters, climate conditions and end-user preferences. The relevant settings are accessible and programmable through the FOR SERVICEMAN menu on the user interface. The user interface menus and settings can be navigated using the touch-sensitive keys.

| Icon | Name | Function |
| --- | --- | --- |
|  | Menu | From the home screen, press Return to the previous page Return to the previous page from a page other than the home screen |
|  | Return | Hold for 2 seconds to return to the home page.(except in For serviceman mode, in USB function mode, in dry connector control mode) |
|  | Confirm | Confirm a selection Save settings Access the next page |
|  | ON/OFF | Turn on/off zone 1/zone 2/DHW individually Press and hold for 3 seconds to turn on/off zone 1 / zone 2 / DHW all at once |
|  | Navigation | Press to activate the cursor which lets you settings. Holding for 1 second enables quick-start adjustments. |

Combinations of buttons：

Press  and  simultaneously for 3 seconds to enter the FOR SERVICEMAN menu.

Menu Structure

Functions may be disabled or unavailable and will not appear on the menu.

FOR SERVICEMAN Menu

For serviceman allows installers to input the system configuration and set the system parameters.

Press  and  simultaneously for 3 seconds to enter the authorization page.

Press  to navigate cursor and press  to adjust the numerical values. The password is 234. Press  to enter For serviceman menu.

Then the following pages will be displayed:

DHW heating setting

      - DHW mode

DHW mode is for configuring an installed DHW tank.

| Setting | Description |
| --- | --- |
| YES | Enable DHW mode if DHW tank is installed. |
| NO | Disable DHW mode if DHW tank is not installed. In this case, no need to define others DHW setting, all other settings in DHW setting will be invisible. |

      - Disinfect, T5S_DISINFECT, t_DI_HIGHTEMP, t_DI_MAX

Disinfect defines whether disinfection function is activated.

| Setting | Description |
| --- | --- |
| YES | Enable DHW tank disinfection function. |
| NO | Disable DHW tank disinfection function. |

T5S_DISINFECT defines the target water temperature of water tank for disinfection function.

t_DI_HIGHTEMP defines how long that disinfection water target temperature is maintained..

t_DI_MAX defines maximum duration of entire disinfection cycle..

Abbreviations:

T5: DHW tank water temperature

      - DHW priority, DHW priority time set, t_DHWHP_RESTRICT, t_DHWHP_MAX

DHW priority defines whether domestic hot water or space heating/cooling is given priority.

| Setting | Description |
| --- | --- |
| YES | When DHW demand and space heating/cooling demand both exist, heat pump will heat the water according to the setting of DHW priority time set, t_DHWHP_RESTRICT, t_DHWHP_MAX |
| NO | When DHW demand and space heating/cooling demand both exist, heat pump will heat the water after space heating/cooling demand is satisfied. |

DHW priority time set defines whether t_DHWHP_RESTRICT (the operation time of heating/cooling mode) is to be considered before switching to DHW mode and conversely whether t_DHWHP_MAX (the operation time of DHW mode) is to be considered before switching to heating/cooling mode.

| Setting | Description |
| --- | --- |
| YES | Enables setting of t_DHWHP_RESTRICT, t_DHWHP_MAX |
| NO | Disables setting of t_DHWHP_RESTRICT, t_DHWHP_MAX |

t_DHWHP_RESTRICT defines the period that heat pump runs in space heating/cooling mode before switching to DHW mode if DHW requirement exists.

t_DHWHP_MAX defines the period that heat pump runs in DWH mode before switching to space heating/cooling mode if space heating/cooling requirement exists.

The diagram below illustrates the effects of t_DHWHP_MAX and t_DHWHP_RESTRICT when DHW PRIORITY and DHW priority time set are enabled.

Abbreviations:

T5: DHW tank water temperature

T5S: DHW tank set temperature

T5stop: Leaving water temperature operating limit of DHW mode

| DHW PRIORITY | DHW PRIORITY TIME SET | t_DHWHP_RESTRICT | t_DHWHP_MAX | Heating/Cooling turns to DHW | DHW turns to Heating/Cooling |
| --- | --- | --- | --- | --- | --- |
| YES | YES | A min | B min | && DHW mode ON && T5<MIN(T5S, T5STOP)-dT5_ON && Heating/Cooling mode operates for A mins | ¦¦ DHW mode OFF ¦¦ T5≥MIN(T5S, T5STOP) ¦¦ DHW mode operates for B mins && Heating/Cooling mode ON |
| YES | NO | - | - | && DHW mode ON && T5<MIN(T5S, T5STOP)-dT5_ON | ¦¦ DHW mode OFF ¦¦ T5≥MIN(T5S, T5STOP) && Heating/Cooling mode ON |
| NO | - | - | - | && DHW mode ON && T5<MIN(T5S, T5STOP)-1 && Heating/Cooling mode OFF | Heating/Cooling mode ON |

Diagram below illustrates the effect of disabling DHW priority time set.

Abbreviations:

T5: DHW tank water temperature

T5S: DHW tank set temperature

T5stop: Leaving water temperature operating limit of DHW mode

      - Pump_D, PUMP_D TIMER, PUMP_D RUNNING TIME, PUMP_D DISINFECT

DHW pump (Pump_D) is installed to circulate the water in the DHW pipe network.

| Setting | Description |
| --- | --- |
| YES | Installation with DHW pump |
| NO | Installation without DHW pump |

PUMP_D TIMER defines whether DHW pump operation schedule, which is defined in the user menu, is activated.

| Setting | Description |
| --- | --- |
| YES | Enables DHW pump run with timer |
| NO | Disables DHW pump run with timer |

PUMP_D RUNNING TIME defines the period that DHW pump operates for each timer.

The diagram below illustrates the effects of PUMP_D RUNNING TIME when Pump_D is installed and PUMP_D TIMER is enable.

PUMP_D DISINFECT defines whether DHW pump operation is activated in disinfection mode.

| Setting | Description |
| --- | --- |
| YES | When heat pump is in disinfection mode and T5S_DISINFECT - T5≤2, DHW pump operates PUMP_D RUNNING TIME+5 minutes T5S_DISINFECT: DHW tank disinfection set temperature T5: DHW tank temperature |
| NO | Disables the DHW pump operation when heat pump is in disinfection mode |

      - dT5_ON

dT5_ON defines water temperature hysteresis of activating heat pump.

When T5S - T5 ≥ dT5_ON and heat pump is within operating ambient temperature range, heat pump provides hot water to the DHW tank.

Abbreviations:

T5: DHW tank water temperature

T5S: DHW set temperature

      - dT1S5

Set leaving water temperature(T1S) for DHW mode is calculated by formula: T1S = T5 + △dT1S5 + dT1S5

T1S: Set leaving water temperature

T5: DHW tank water temperature

△dT1S5: Temperature modification value related to DHW tank water temperature(T5)

| T5 | T5<30℃ | 30℃≤T5<43℃ | 43℃≤T5 |
| --- | --- | --- | --- |
| △dT1S5 | 6 | 4 | 0 |

dT1S5: Temperature difference between Set leaving water temperature and tank water temperature modification value.

      - T4DHWMAX, T4DHWMIN

T4DHWMAX defines the ambient temperature above which heat pump and AHS/IBH may have different actions.

When T4DHWMAX≤T4 and T4DHWMAX<43℃, both compressor and AHS/IBH stop running.

When T4HMAX≤T4 and T4DHWMAX=43℃, compressor runs with lowest frequency and AHS/IBH runs according to user demand.

T4DHWMIN defines the ambient temperature below which heat pump stops, while AHS/IBH/TBH can run if dT1_AHS_ON/dT1_IBH_ON/dT5_ON is satisfied. (The minimum T4DHWMIN is set to -25 °C)

The diagram below illustrates the effects of T4DHWMAX and T4DHWMIN.

Abbreviations:

HP: Heat pump

TBH: DWH tank immersion heater

AHS: Auxiliary heat source

IBH: Electric heater

Cooling setting

      - Cooling mode

Cooling mode is for configuring cooling operation.

| Setting | Description |
| --- | --- |
| YES | Enables cooling mode if space cooling terminals are installed. |
| NO | Disables cooling mode if space cooling terminals are not installed. In this case, no need to define other settings in Cooling mode, all other settings in Cooling mode will be invisible. |

      - t_T4_FRESH_C

t_T4_FRESH_C defines the ambient temperature detection refresh cycle for climate curves.

      - T4CMAX, T4CMIN

T4CMAX defines ambient temperature above which the heat pump operates with lowest compressor frequency.

T4CMIN defines ambient temperature below which heat pump will not operate.

The diagram below illustrates the effects of T4CMAX and T4CMIN.

Abbreviations:

T4: Outdoor ambient temperature

      - dT1SC

dT1SC defines water temperature hysteresis of activating heat pump.

When T1 – T1S ≥ dT1SC and heat pump is within operating ambient temperature range, heat pump provides chilled water to space cooling terminals.

Abbreviations:

T1: Leaving water temperature

T1S: Set leaving water temperature

T1Stop: Leaving water temperature operating limit of cooling mode

      - dTSC

dTSC define room temperature hysteresis of activating heat pump. dTSC is only applicable if YES is selected for Room temp. in the Temp. type setting.

When Ta – TS ≥ dTSC and heat pump is within operating ambient temperature range, heat pump provides chilled water to space cooling terminals.

Abbreviations:

Ta: Actual room temperature

TS: Room setting temperature

      - Zone 1 C-emission, Zone 2 C-emission

Zone 1 C-emission defines the terminal type of zone 1.

| Setting | Description |
| --- | --- |
| FCU | Fan coil unit |
| FLH | Floor heating loop |
| RAD | Radiator |

Zone 2 C-emission defines the terminal type of zone 2.

| Setting | Description |
| --- | --- |
| FCU | Fan coil unit |
| FLH | Floor heating loop |
| RAD | Radiator |

Heating setting

      - Heating mode

Heating mode is for configuring heating operation.

| Setting | Description |
| --- | --- |
| YES | Enable heating mode if space heating terminals are installed. |
| NO | Disable heating mode if space heating terminals are not installed. In this case, no need to define other settings in Heating mode, all other settings in Heating mode will be invisible. |

      - t_T4_FRESH_H

t_T4_FRESH_H defines the refresh time of heating mode climate temperature curve.

      - T4HMAX, T4HMIN

T4HMAX defines the ambient temperature above which heat pump and AHS/IBH may have different actions.

When T4HMAX≤T4 and T4HMAX<35, both compressor and AHS/IBH stop running. 
When T4HMAX≤T4 and T4HMAX=35, compressor runs at lowest frequency and AHS/IBH runs according to user demand.

T4HMIN defines the ambient temperature below which heat pump stops, while AHS/IBH can run if dT1_AHS_ON/dT1_IBH_ON is satisfied.

Diagram below illustrates the effects of T4HMAX and T4HMIN.

Abbreviations:

T4: Outdoor ambient temperature

AHS: Additional heat source

IBH: Electric heater

      - dT1SH

dT1SH defines water temperature hysteresis of activating heat pump.

When T1≤T1S - dT1SH and heat pump is within operating ambient temperature range, heat pump provides hot water to the space heating terminals.

      - dTSH

dTSH defines room temperature hysteresis of stopping heat pump. dTSH is only applicable if YES is selected for Room temp. in the Temp. type setting.

When TS – Ta ≥ dTSH and heat pump is within operating ambient temperature range, heat pump provides hot water to the space heating terminals

Abbreviations:

Ta: Actual room temperature

TS: Room setting temperature

      - Zone 1 H-emission, Zone 2 H-emission

The same as Zone 1 C-emission and Zone 2 C-emission

      - Force defrost

Force defrost enabled heat pump enters defrost mode by manual operation when heat pump runs for 10min and air-side heat exchanger outlet temperature T3<0℃ lasts for more than 6min.

| Setting | Description |
| --- | --- |
| YES | Enables Force defrost function |
| NO | Disables Force defrost function |

Auto mode setting

      - T4AUTOCMIN, T4AUTOHMAX

T4AUTOCMIN defines the ambient temperature below which the heat pump will not provide chilled water for space cooling in auto mode.

T4AUTOHMAX defines the ambient temperature above which the heat pump will not provide hot water for space heating in auto mode.

The diagram below illustrates the effects of T4AUTOCMIN, T4AUTOHMAX, T4CMAX and T4HMIN.

Abbreviations:

AHS: Additional heat source

IBH: Backup electric heater

T4CMAX: The ambient temperature above which heat pump operates with lowest compressor frequency

T4HMIN: The ambient temperature below which the heat pump will not operate in heating mode

Temp. type setting

The Temp. type setting is used for selecting whether the water flow temperature or room temperature is used to control the ON/OFF of the heat pump. In this case, 7.3.6 Room thermostat setting should be defined as NO.

Room temperature control

Water temperature control

Room temperature control

      - Water flow temp.

Water flow temp. defines whether heat pump is controlled by leaving water temperature.

| Setting | Description |
| --- | --- |
| YES | Heat pump is controlled by leaving water temperature. |
| NO | Heat pump is not controlled by leaving water temperature. |

      - Room temp.

Room temp. defines whether heat pump is controlled by room temperature detected by the temperature sensor inside the wired controller.

| Setting | Description |
| --- | --- |
| YES | Heat pump is controlled by room temperature no matter what is the setting of 7.3.5.1 Water flow temp. In this case, the target water flow temperature will be calculated from climate curves. |
| NO | Heat pump is not controlled by room temperature. |

      - Double zone

Double zone defines the number of zones.

| Setting | Description |
| --- | --- |
| YES | Double-zone control |
| NO | Single-zone control |

Figure below illustrates the effects of different combinations in Temp. type setting.

For single-zone control

| WATER FLOW TEMP. | ROOM TEMP. | DOUBLE ZONE | Zones control |
| --- | --- | --- | --- |
| YES | NO | NO | Zone 1: Water temperature control |
| NO | YES | NO | Zone 1: Room temperature control |

For Double-zone control

| WATER FLOW TEMP. | ROOM TEMP. | DOUBLE ZONE | Zones control |
| --- | --- | --- | --- |
| YES | YES | YES | Zone 1: Water temperature control |
|  |  |  | Zone 2: Room temperature control |
| YES | NO | YES | Zone 1: Water temperature control |
|  |  |  | Zone 2: Water temperature control |

Room thermostat setting

Room thermostat can be an alternate heat pump control solution.

| Setting | Description | Wired controller is used to |
| --- | --- | --- |
| NO | - NON - Without room thermostats (means Temp. type setting is valid) | - Control heat pump ON/OFF - Define water temperature - Define mode (heating/cooling/auto mode) |
| MODE SET | - MODE SET - Room thermostat provides separate heating/cooling switch signal to control heat pump ON/OFF - One zone control - All timers are invalid except DHW timers. | - Define water temperature |
| ONE ZONE | - ONE ZONE - Room thermostat provides switch signal to control heat pump ON/OFF - One zone control - All timers are invalid except DHW timers. | - Define water temperature - Define mode (heating/cooling mode) |
| DOUBLE ZONE | - DOUBLE ZONE - Room thermostat provides switch signal to control heat pump ON/OFF - Double zones control - All timers are invalid except DHW timers. | - Define water temperature - Define mode (Only for heating mode) |

If Room thermostat setting is defined as MODE SET, the interface appears:

Mode set priority defines whether cooling mode or heating mode takes priority.

| Setting | Description |
| --- | --- |
| Heating | When heating and cooling switch signal are closed simultaneously, the heat pump runs in heating mode. |
| Cooling | When heating and cooling switch signal are closed simultaneously, the heat pump runs in cooling mode. |

Other Heat Source Menu

      - IBH FUNCTION, dT1_IBH_ON, t_IBH_DELAY, T4_IBH_ON, P_IBH1, P_IBH2

IBH FUNCTION defines backup heater function.

| Setting | Description |
| --- | --- |
| YES | IBH is used for heating mode |
| NO | IBH is used for heating mode and DHW mode |

dT1_IBH_ON defines water temperature hysteresis of activating electric heater. When T1S - T1 ≥ dT1_IBH_ON the backup electric heater is on.

T1S: Heat pump leaving water set temperature

T1: Heat pump leaving water temperature

t_IBH_DELAY defines the delayed start-up time of electric heater. Electric heater will turn on t_IBH_DELAY minutes later after compressor starts.

T4_IBH_ON defines the ambient temperature below which the backup electric heater is on.

Note: Only when dT1_IBH_ON, t_IBH_DELAY and T4_IBH_ON are met at the same time then electric heater turns on.

Diagram below illustrates the effects of T4_IBH_ON, T4HMIN and T4HMAX.

Abbreviations:

T4: Outdoor ambient temperature

IBH: Electric heater

T4HMIN: The ambient temperature below which the heat pump will not operate in heating mode.

T4HMAX: The ambient temperature above which the heat pump will operate heating mode with lowest compressor frequency.

P_IBH1 defines heating capacity of IBH1, which is used for energy consumption statistics.

P_IBH2 defines heating capacity of IBH2, which is used for energy consumption statistics.

      - AHS FUNCTION, AHS_PUMP_I CONTROL, dT1_AHS_ON, t_AHS_DELAY, T4_AHS_ON

AHS FUNCTION defines auxiliary heat source function.

| Setting | Description |
| --- | --- |
| NO | Without Auxiliary heat source |
| Heating | Auxiliary heat source is used for heating mode |
| Heating and DHW | Auxiliary heat source is used for heating mode and DHW mode |

AHS_PUMP_I CONTROL select the Pump_I operating status when only auxiliary heat source runs.

| Setting | Description |
| --- | --- |
| Run | Pump_I runs when auxiliary heat source runs only. |
| Not run | Pump_I does not run when auxiliary heat source runs only. In this case, please confirm there is an additional pump running for auxiliary heat source. |

dT1_AHS_ON defines water temperature hysteresis of activating auxiliary heat source. When T1S - T1 ≥ dT1_AHS_ON the additional heat source is on.

T1S: Heat pump set leaving water temperature

T1: Heat pump leaving water temperature

t_AHS_DELAY defines the delayed start-up time of auxiliary heat source. Auxiliary heat source will turn on t_AHS_DELAY minutes later after compressor starts.

T4_AHS_ON defines the ambient temperature below which the auxiliary heat source is on.

Note: Only when dT1_AHS_ON, t_AHS_DELAY and T4_AHS_ON coincide will then auxiliary heat source turn on.

The diagram below illustrates the effects of T4_AHS_ON, T4HMIN and T4HMAX.

Abbreviations:

T4: Outdoor ambient temperature

AHS: Auxiliary heat source

T4HMIN: The ambient temperature below which the heat pump will not operate in heating mode.

T4HMAX: The ambient temperature above which the heat pump will operate in heating mode with lowest compressor frequency.

      - EnSWITCHPDC, GAS_COST, ELE_COST

EnSWITCHPDC defines whether heat pump and additional heat source switch automatically based on economic performance and system high efficiency.

| Setting | Description |
| --- | --- |
| NO | Disable EnSWITCHPDC function, T4_AHS_ON need to be defined manually. Additional heat source may work with heat pump depends on the water temperature and heat pump status. |
| YES | Enable EnSWITCHPDC function, T4_AHS_ON is calculated according to price of gas and electricity and the efficiency of boiler and heat pump. Only Additional heat source works at ambient temperature of T4_AHS_ON because of the economic performance and system high efficiency. |

GAS_COST defines gas price

ELE_COST defines electricity price

      - MAX_SETHEATER, MIN_SETHEATER, MAX_SIGHEATER, MIN_SIGHEATER

When “AHS1” port and “AHS2” port of main control PCB are connected with auxiliary heat source “ON/OFF” signal, auxiliary heat source leaving water temperature automatically change as voltage changes.

MAX_SETHEATER sets the maximum water temperature of auxiliary heat source.

MIN_SETHEATER sets the minimum water temperature of auxiliary heat source.

MAX_SIGHEATER sets the voltage corresponding to the maximum water set temperature of auxiliary heat source.

MIN_SIGHEATER sets the voltage corresponding to the minimum water set temperature of auxiliary heat source.

Diagram below illustrates the effects of MAX_SETHEATER, MIN_SETHEATER, MAX_SIGHEATER and MIN_SIGHEATER.

      - TBH FUNCTION, dT5_TBH_OFF, t_TBH_DELAY, T4_TBH_ON, P_TBH

TBH FUNCTION defines whether tank booster heater function is activated.

| Setting | Description |
| --- | --- |
| YES | Enables tank booster heater function |
| NO | Disables tank booster heater function |

dT5_TBH_OFF defines water temperature hysteresis of inactivating tank booster heater when heat pump malfunctions.

When T5 > Min(T5S+dT5_TBH_OFF, 70°C), the tank booster heater is off.

T5S: Domestic hot water tank set temperature

t_TBH_DELAY defines the delayed start-up time of tank booster heater. Tank booster heater will turn on t_TBH_DELAY minutes later after compressor starts.

T4_TBH_ON defines the ambient temperature below which the tank booster heater is on.

Note: Only when t_TBH_DELAY, T4_TBH_ON are met at the same time then tank booster heater turns on.

P_TBH defines the power input of tank booster heater, which is used for energy consumption statistics.

Diagram below illustrates the operation of heat pump and tank booster heater of DHW mode.

Abbreviations:

T5S: DHW set temperature

T5stop: DHW mode leaving water temperature operating limit

TBH: Immersion heater

      - Solar function, Solar control, Deltasol

Solar function defines whether the heating system is equipped with solar function.

| Setting | Description |
| --- | --- |
| NO | Without solar function. |
| Solar and HP | With solar function and heat pump. |
| Only solar | With only solar function. |

Solar control defines the control type of solar pump

| Setting | Description |
| --- | --- |
| Tsolar | Solar pump (Pump_S) is controlled by solar temperature sensor |
| SL1SL2 | Solar pump (Pump_S) is controlled by SL1SL2 signal |

Deltasol defines temperature hysteresis of activating solar pump (Pump_s).

When Tsolar > T5 + Deltasol, T5 < 79℃ and DHW mode is ON, the solar pump activates.

Service call

Phone number and Mobile number define after-sales service contact numbers. Press  to navigate cursor and press   to adjust the numerical values. The maximum length of the phone numbers is 15 digits.

Restore factory settings

Restore factory settings is used to restore all the parameters (including energy metering data and WLAN setting) set in the user interface to factory defaults.

On selecting YES, the process of restoring all settings to factory defaults begins and progress is displayed as a percentage.

Test run

Test run is used to do the point check and check that air purge function, circulation pump, cooling mode, heating mode and DHW mode are all operating correctly. If any error code is displayed during the test run operation, the cause should be investigated.

During test run, all buttons except  are invalid. If you want to turn off the test run, please press . For example, when the unit is in air purge mode, after you press , the following page will be displayed:

      - Point check

The POINT CHECK menu is used to check the operation of indiviDouble components. Use   to scroll to the components you want to check and press  to toggle the on/off state of the component. If a valve does not turn on/off or a pump/heater does not operate when their on/off state is toggled, please check the connection between component and main PCB and make sure components’ status is normal.

      - Air purge

Once installation is complete, it is important to run the air purge function to remove any air which may be present in the water piping which could cause malfunctions during operation. Before running Air purge mode, make sure that the air purge valve is open. Pump_I will run according to the output and running time that has been set.

Air purge defines whether the function is activated.

Air purge Pump_I output defines the Pump_I output capacity.

Air purge running time defines the period that Pump_I operates during the air purge process.

Status check allows installers to check the real-time operation parameters of air purge operation.

      - Circulated pump running

Circulated pump running operation is used to check the operation of the circulation pump.

When circulation pump running is turned on, all running components will stop.

Circulated pump running operation is used to check the operation of the circulation pump.

When circulation pump running is turned on, all running components will stop.

When the unit received signal that indicates Circulated pump running =ON:

- SV1 will turn on after 30 secs;

- Pump_I will turn on after 60 secs.

- Pump_I will turn off after 240 secs.

- SV1 will turn off and the SV2 will turn on after 270 secs.

- Pump_I & pump_O will turn on after after 30 secs

If E8 occurs during these processes, the unit will stop Circulated pump running mode immediately

      - Cooling running

The Cooling running operation is used to check the operation of the system in space cooling mode.

During the Cooling running operation, the leaving water set temperature is 7°C. The current actual leaving water temperature is displayed on the user interface. The unit operates until the leaving water temperature drops to the set temperature or the next command is received.

      - Heating running

The Heating running operation is used to check the operation of the system in space heating mode.

During Heating running operation, the default target outlet water temperature is 35°C. The IBH (backup heater) will turn on after the compressor runs for 10 min. The IBH will run for 3 minutes and then turn off. The heat pump will operate until the water temperature increases to a certain value or the next command is received.

      - DHW running

The DHW running operation is used to check the operation of the system in DHW mode.

During DHW running operation, the default target temperature of the domestic water is 55°C. The TBH (tank boost heater) will turn on after the compressor runs for 10min. The TBH will turn off 3 minutes later. The heat pump will operate until the water temperature increases to a certain value or the next command is received.

Special Function

      - Preheating for floor

Preheating for floor function provides mild heat to the underfloor water piping for the first time during seasonal heating, diminish the risk of damage to the floor and piping system.

| Setting | Description |
| --- | --- |
| 0 | Disables preheating for floor function |
| 1 | Enables preheating for floor function |

T1S defines heat pump leaving water temperature in preheating

T_ARSTH defines running time for first preheating of the floor

Elapsed time is the period that Preheating for floor function had run

Tw_out temp. is the current leaving water temperature

Diagram below illustrates the operation of Preheating for floor function

Abbreviations:

T1: Leaving water temperature

dT1SH: Water temperature hysteresis of activating heat pump.

t_interval_H: The delayed start-up time of compressor in heating mode.

      - Floor drying up

For newly-installed under-floor heating systems, floor drying up is necessary to remove moisture from the flooring and subfloor to prevent warping or rupture. The heat pump provides mild heat to the concrete or other structural material around the underfloor water piping for a certain period of time to accelerate the process of getting rid of moisture. During floor drying up operation, the temperature of the floor would be increased gradually. In the event of a heat pump malfunction, floor drying up mode will continue if a backup electric heater and/or auxiliary heat source is available and configured to support space heating mode.

There are three phases to the floor drying up operation:

- Phase 1: gradually temperature increase to the peak temperature

- Phase 2: maintain peak temperature

- Phase 3: gradually temperature decrease from the peak temperature

Floor drying up

| Setting | Description |
| --- | --- |
| 0 | Disables floor draying up function |
| 1 | Enables floor draying up function |

t_Dryup defines the duration of Phase 1.

t_Highpeak defines the duration of Phase 2.

t_Drydown defines the duration of Phase 3.

t_Drypeak defines the heat pump leaving water temperature of Phase 2.

Start time defines the floor drying up operation start time.

Start date defines the floor drying up operation start date.

Auto restart

Auto restart sets whether or not the unit re-applies the mode and unit status settings when the power returns following a power failure.

If 7.3.6 Room thermostat setting is defined as not 0, Auto restart function will not be applicable.

Auto restart cooling/heating mode

| Setting | Description |
| --- | --- |
| NO | Disables auto restart cooling/heating mode |
| YES | Enables auto restart cooling/heating mode |

Auto restart DHW mode

| Setting | Description |
| --- | --- |
| NO | Disables auto restart DHW mode |
| YES | Enables auto restart DHW mode |

Power input limitation

Power input limitation makes the unit suitable for a variety of current supplies. There are 8 configurations for user to choose according to the maximum allowable access current. If the unit will operate at larger current input, 1 should be selected. If the unit will operate at a lower current input, 2-8 should be selected and the power input and capacity will decrease.

Power limitation function

| Setting | Model |  |  |  |
| --- | --- | --- | --- | --- |
|  | 26kW | 30kW | 35kW | 40kW |
| 1 | 23A | 26A | 29A | 29A |
| 2 | 22A | 25A | 28A | 28A |
| 3 | 21A | 24A | 27A | 27A |
| 4 | 20A | 23A | 26A | 26A |
| 5 | 19A | 22A | 25A | 25A |
| 6 | 18A | 21A | 24A | 24A |
| 7 | 17A | 20A | 23A | 23A |
| 8 | 16A | 19A | 22A | 22A |

Input definition

INPUT DEFINE defines sensor and function preferences during installation.

M1 M2 defines the function of M1M2 port

| Setting | Description |
| --- | --- |
| Remote ON/OFF | Remote ON/OFF control of heat pump |
| TBH ON/OFF | Remote ON/OFF control of tank booster heater |
| AHS ON/OFF | Remote ON/OFF control of auxiliary heat source |

Smart grid defines whether SMART GRID control signal is connected to hydronic PCB.

| Setting | Description |
| --- | --- |
| NO | Disables Smart grid function |
| YES | Enables Smart grid function |

T1 T2 defines control options of Port T1 T2

| Setting | Description |
| --- | --- |
| NO | Installation without MH-kit |
| RT/Ta_PCB | Installation with MH-kit |

Tbt defines whether balance tank temperature sensors are installed in the balance tank.

| Setting | Description |
| --- | --- |
| NO | Installation without balance tank temperature sensor (Tbt) |
| YES | Installation with balance tank temperature sensor (Tbt) |

P_X PORT can be defined as defrosting signal or alarm signal according to customers’ demand.

| Setting | Description |
| --- | --- |
| Defrost | Defrosting signal |
| Alarm | Alarm signal |

Cascade setting

PER_START sets the start-up percentage of multiple units for the first time start-up after power on. For example:

| Total units | PER_START | Starting units |
| --- | --- | --- |
| 6 | 50% | 3 |
| 6 | 30% | 2 |

TIME_ADJUST sets the judgment period of adding and subtracting units

HMI address setting

HMI ADDRESS FOR BMS sets the HMI address code for BMS (only valid for master controller)

STOP BIT sets upper computer stop bit(1: STOP BIT1; 2:STOP BIT2)

| Setting | Description |
| --- | --- |
| 1 | Stop bit 1 |
| 2 | Stop bit 2 |

Common setting

      - t_DELAY PUMP

t_DELAY PUMP defines the delayed stop time of Pump_I. Pump_I will stop t_DELAY PUMP minutes later after compressor stops base on system temperature equalization consideration.

      - t1_ANTILOCK PUMP, t2_ANTILOCK PUMP RUN, t1_ANTILOCK SV, t2_ANTILOCK SV RUN

Antilock operation prevent components from sticking to result in system fail.

t1_ANTILOCK PUMP defines the interval time that Pump_I, Pump_O and Pump_C runs in order to antilock

t2_ANTILOCK PUMP RUN defines the running time for Pump_I, Pump_O and Pump_C antilock operation

t1_ANTILOCK SV defines the interval time that SV1, SV2 and SV3 valve works in order to antilock

t2_ANTILOCK SV RUN defines the running time for SV1, SV2 and SV3 valve antilock operation

      - Ta-adj

Ta-adj is an correction value for room temperature sensor(Ta) which is inside the wired controller. The display room temperature value is equal to Ta + Ta-adj.

      - PUMP_I_SLIENT OUTPUT

PUMP_I_SLIENT OUTPUT can decrease water pump maximum output in order to decrease the noise of heat pump.

      - Energy metering

Energy metering allows user to check energy data of day, week, month and year.

| Setting | Description |
| --- | --- |
| NO | Disable energy metering function |
| YES | Enable energy metering function |

      - Pump_O

Pump_O defines Zone 1 pump(Pump_O) control type.

| Setting | Description |
| --- | --- |
| ON | Pump_O keeps running |
| Auto | Pump_O operation is controlled by heat pump |

      - Glycol, Glycol concentration

Glycol defines whether the unit has added glycol.

| Setting | Description |
| --- | --- |
| 0 | Without glycol |
| 1 | With glycol |

Glycol concentration Define the concentration of glycol added to the unit.

The concentration setting of glycol will affect the correction of the water flow of the unit

Clear energy data

Once selecting YES, All energy metering data is clear.

Intelligent function settings

      - Energy correction

The actual installation scenario would be different from one to another. The energy metering calculation of the unit could deviate slightly due to the actual installation.

Energy correction is to offset the deviation of the energy metering calculation of the unit. Value from -50% to 50%, default is 0. It is applied for Heating, Cooling and DHW.

The final energy data = original data * (1+ Energy correction)

C2 fault restore

For the unit with IBH(internal backup heater), when C2 error occurs, please follow C2 troubleshooting guide of Part4 Diagnosis and Troubleshooting. If necessary, select YES to restore C2 code.

Operation parameter

Operation parameter is for reviewing the operation parameters. The interface below is for reference and different units’ state correspond to different parameter values.

Operation for entering Operation parameter：

Step 1: Home page

Step 2: Press “”

Step 3: Select “Unit status”

Step 4: Select “Operation parameter”

Step 5: Press

Part of operation parameter may be disabled or unavailable and will not appear on the menu.

OTA (Over-The-Air) guideline

HIM software version is above V1.0.0.95

If your wire controller is not connected to the mobile APP, you need to connect to Internet. (Set personal hotspot with smart phone, hotspot name as: SMARTOTA Password: ota12345. And place the smart phone near the wired controller)

If your wire controller is already connected to the mobile APP, you can follow the following procedure directly.

Step 1: Long press "≡"and "˅" for about 4 seconds in wire controller homepage.

Step 2: A password for OTA is needed, use the arrow button to change the password as 999.

Then press "O" to confirm to start the OTA.

Step 3:HIM will display “Updating, please wait...”, a progress percentage will be shown.

When the OTA progress is finish, the HIM will auto restart. Check whether the OTA is succeeded and software of the HIM had been updated.

USB Function Field Settings

USB function helps you easily transmit parameters and program. When USB device is connected to CN4 port of main control PCB, the USB function interface appears automatically on the wired controller.

| Main control PCB |  |  |  |
| --- | --- | --- | --- |
|  |  | CN4 USB port |  |
| USB function interface |  |  |  |
| Sub-function 1: Copy setting parameters from wired controller to USB disk Sub-function 2: Paste setting parameters from USB disk to wired controller |  |  | Sub-function 3: Paste hydraulic system program Sub-function 4: Paste refrigerant system program |

Sub-function 1:

Once the process finishes successfully, the parameter file “M_Thermal_Config(Prohibit to rewrite).csv” will be generated on the USB device. If you want to change the parameter settings on a computer, please remember to only change the value of column C (red frame below) and do not change any other content or the file name.

Sub-function 2:

Please make sure there is only one parameter file on the USB device before using this function.

Sub-function 3:

Please make sure there is only one applicable hydraulic system program on the USB device before using this function.

Sub-function 4:

Please make sure there is only one applicable refrigerant system program in the USB disk before using this function.

Press to choose the item and press  to confirm your choice. A progress indicator will then appear as shown below.

During this process, all buttons are non-operational.

When the process finishes, a pop-up window with the word “Success” will appear briefly and the unit stops. At this point, remove the USB device and restart the unit.

Should the process fail, pop-up window with the word “Fail” will appear briefly. The system program remains unchanged.

If the process stalls, please remove the USB device and reinsert it per the operation above.