Part 4

Diagnosis and Troubleshooting

1 Service Information	62

2 Electric wiring diagram	70

3 Electric Control Box Layout	71

4 Outdoor Unit PCBs	72

5 Error Code Table	82

6 Troubleshooting	85

7 Discharge / Suction pressure and temperature range	141

8 Appendix to Part 4	142

Service Information

- These instructions are exclusively intended for qualified contractors and authorized installers

- Work on the refrigerant circuit with flammable refrigerant in safety group A3 may only be carried out by authorized heating contractors. These heating contractors must be trained in accordance with EN 378 Part 4 or IEC 60335-2-40, Section HH. The certificate of competence from an industry accredited body.

- Brazing/soldering work on the refrigerant circuit may only be carried out by contractors certified in accordance with ISO 13585 and AD 2000, Datasheet HP 100R. And only by contractors qualified and certified for the processes to be carried out. The work must fall within the range of applications purchased and be carried out in accordance with the prescribed procedures. Soldering/brazing work on accumulator connections requires certification of personnel and processes by a notified body according to the Pressure Equipment Directive (2014/68/EU).

- Work on electrical equipment may only be carried out by a qualified electrician.

- Before initial commissioning, all safety relevant points must be checked by the particular certified heating contractors. The system must be commissioned by the system installer or a qualified person authorized by the installer.

DANGER！

Label for Refrigerant Presence

Equipment should be provided with a label stating that it has been de-commissioned and emptied of refrigerant. The label should be dated and signed. Ensure that proper labels are pasted on the equipment stating the equipment contains flammable refrigerant

Leak Detection Methods

The following leak detection methods are deemed acceptable for systems containing flammable refrigerants. An electronic leak detector should be used to detect flammable refrigerants, but its sensitivity may not be adequate, or the detector may need re-calibration. (Detection equipment should be calibrated in a refrigerant-free area.) Ensure that the detector is not a potential source of ignition and is suitable for the refrigerant. Leak detection equipment should be set at a percentage of the LFL of the refrigerant and should be calibrated to be suitable for the refrigerant employed. The appropriate percentage of gas (25% maximum) is confirmed. Leak detection fluids are suitable for use with most refrigerants but detergents containing chlorine should not be used as the chlorine may react with the refrigerant and corrode the copper pipes. If a leak is suspected, all naked flames should be removed or extinguished. If a leakage of refrigerant is found and brazing is required, all of the refrigerant should be recovered from the system, or isolated (by means of shut off valves) in a part of the system that is remote from the leak. Oxygen free nitrogen (OFN) should then be purged through the system both before and during the brazing process.

Check of Refrigeration Equipment

Where electrical components are to be changed, they should be fit for the intended purpose and comply with the correct specifications. Always follow the manufacturer’s maintenance and service guidelines. In case of any doubt, consult the manufacturer’s technical department for assistance. Check installations using flammable refrigerants.

- The amount of refrigerant to be charged depends on the size of the room where the refrigerant-containing parts are installed.

- The ventilation machinery and outlets should work adequately and be not obstructed.

- If an indirect refrigerating circuit is used, the secondary circuits should be checked for any refrigerant; Markings on the equipment should be visible and legible.

- Illegible markings and signs should be corrected.

- Refrigeration pipes or components should be installed in positions where they are unlikely to be exposed to any substance that may corrode refrigerant-containing components, unless the components are constructed of materials that are inherently resistant to corrosion or are suitably protected from corrosion

Check of Electrical Devices

Repair and maintenance of electrical components should include initial safety checks and component inspection procedures. If a fault exists and could compromise safety, no electrical supply should be connected to the circuit until it is satisfactorily dealt with. If the fault cannot be corrected immediately but it is necessary to continue operation, an adequate temporary solution should be adopted. This should be reported to the owner of the equipment so all parties are advised. Repair and maintenance of electrical components should include initial safety checks and component inspection procedures. If a fault exists and could compromise safety, no electrical supply should be connected to the circuit until it is satisfactorily dealt with.

If the fault cannot be corrected immediately but it is necessary to continue operation, an adequate temporary solution should be adopted. This should be reported to the owner of the equipment so all parties are advised. Initial safety checks should include the following:

- The capacitors should be discharged in a safe manner to avoid sparking risks

- No live electrical components and wiring can be exposed during the system charging, recovery or purging. Earth bonding should be continuous

- Earth bonding should be continuous

Repair of Sealed Components

- During repair of sealed components, all electrical supplies should be disconnected from the equipment being worked upon prior to any removal of sealed covers. If it is absolutely necessary to have an electrical supply connected with the equipment during servicing, a permanently operating form of leak detection should be located at the most critical point to warn of a potentially hazardous situation.

- Particular attention should be paid to the following to ensure that, by working on electrical components, the casing is not altered in such a way that Protection is compromised. This should include damage to cables, an excessive number of connections, terminals not made as per original specifications, damage to seals, and incorrect fitting of glands.

- Ensure that all apparatuses are mounted securely.

- Ensure that seals or sealing materials have not degraded such that they can no longer prevent the ingress of flammable atmospheres. Parts for replacement should be in accordance with the manufacturer s specifications.

- The use of silicon sealant may inhibit the effectiveness of some types of leak detection equipment. Intrinsically safe components do not have to be isolated prior to working on them.

Repair of Intrinsically Safe Components

Do not apply any permanent inductive or capacitance loads to the circuit without ensuring that such loads will not exceed the permissible voltage or current permitted for the equipment in use. Intrinsically safe components are the only types that can be worked on when the components live in a flammable atmosphere. The test apparatus should be provided with the correct rating. Replace components only with parts specified by the manufacturer. Other parts may result in the ignition of refrigerant in the atmosphere caused by a leak.

Transportation and Marking

Transport the equipment containing flammable refrigerants in accordance with the transport regulations. Mark the equipment with signs in compliance with local regulations.

Disposal

General

- Components and accessories of the unit are not ordinary domestic wastes.

- The unit, compressors, and motors, etc. can only be disposed of by qualified specialists.

- This unit uses hydrofluorocarbon that can only be disposed of by qualified specialists

Packaging

- Dispose of the packaging properly.

- Observe all relevant regulations

Refrigerant Removal, Evacuation, Charge, Recovery, and Unit Decommissioning

Due to the feature of the R290 refrigerant, only carry out work when you have specific expert refrigeration knowledge and are competent for handling R290 refrigerant.

Work on the refrigerant circuit with flammable refrigerant in safety group A3 may only be carried out by authorized heating contractors.

WARNING！

      - Removal and evacuation

When breaking into the refrigerant circuit for repair or any other purpose, follow the conventional procedures. However, it is important to follow the best practice since flammability should be considered. Operate as per the following procedure:

- Remove refrigerant;

- Purge the circuit with inert gas;

- Evacuate;

- Purge the circuit again with inert gas;

- Open the circuit by cutting or brazing

The refrigerant charged should be recovered and put in correct recovery cylinders. The system should be flushed with OFN to guarantee the unit safety. This process may need to be repeated several times. Compressed air or oxygen should not be used.

Flushing should be achieved by filling the system with OFN until the working pressure is achieved before venting to the atmosphere, and recovering the system to a vacuum. This process should be repeated until no refrigerant exists in the system.

Upon the final OFN charge, the system should be vented down to reach the atmospheric pressure to start the work.

This operation is absolutely vital if brazing operations on the pipe-work are to take place.

Ensure that the outlet of the vacuum pump is not closed to any ignition sources and adequate ventilation is available.

      - Charging procedures

In addition to conventional charging procedures, the following requirements should be followed:

- Ensure that contamination of different refrigerants does not occur when charging equipment is used. Hoses or lines should be as short as possible to minimize the amount of refrigerant contained in them.

- Earth the refrigeration system prior to charging the system with refrigerant.

- Label the system upon completion of the charging (if the system has not been labeled).

- Extreme care should be taken not to overfill the refrigeration system.

- Prior to recharging the system, test it with OFN. The system should be leak tested upon completion of charging but prior to commissioning. Carry out a follow-up leak test before leaving the site.

      - Recovery

When removing refrigerant from the system, either for service or decommissioning, we recommend you remove all refrigerants safely by following the best practice.

When transferring refrigerant into cylinders, only use appropriate refrigerant recovery cylinders. Ensure that a proper number of cylinders are available for accommodating all the refrigerant. All cylinders to be used are designated and labeled for the recovered refrigerant (i.e., special cylinders for the recovery of refrigerant). The cylinders should be complete with pressure relief valves and associated shut-off valves that work properly.

Empty recovery cylinders should be evacuated and, if possible, cooled before the recovery starts.

The recovery equipment should work properly with a set of instructions concerning the equipment at hand, and should be suitable for the recovery of flammable refrigerants. In addition, a set of calibrated weighting scales should be available and work properly. Hoses should be complete with leak-free disconnection couplings and in good conditions. Before using the recovery equipment, check and verify that it works properly and has been properly maintained, and that any associated electrical components are sealed to prevent ignition in the event of a refrigerant leakage. Consult the manufacturer in case of any doubt.

The recovered refrigerant should be returned to the refrigerant supplier in correct recovery cylinders, with the relevant Waste Transfer Note arranged. Do not mix refrigerants in recovery units, especially in cylinders.

If compressors or compressor oils are to be removed, ensure that they have been evacuated to an acceptable level to ensure that flammable refrigerant does not remain within the lubricant. Carry out the evacuation process before returning the compressor to the suppliers. To accelerate this process, you can only heat the compressor body electrically. Safety drain oil from the system.

      - Decommissioning

Prior to this procedure, the technician should be completely familiar with the equipment and all its details. It is recommended that all refrigerants be recovered safely. Prior to the recovery, an oil and refrigerant sample should be taken for case analysis before re-use of reclaimed refrigerant. Electrical power should be available before the task is commenced.

- Be familiar with the equipment and its operation.

- Isolate the system electrically

- Before attempting the procedure ensure that:

- Mechanical handling equipment is available, if required, for handling refrigerant cylinders.

- All personal protective equipment should be available and used securely.

- The recovery process should be supervised at all time by a competent person.

- Recovery equipment and cylinders should conform to the appropriate standards.

- Pump down the refrigerant system, if possible.

- If a vacuum is not possible, provide a manifold to remove the refrigerant from various parts of the system.

- Ensure that the cylinders are situated on the scales before the recovery starts.

- Start the recovery machine and operate it in accordance with the manufacturer's instructions.

- Do not overfill the cylinders (for no more than 80% of the volume).

- Do not exceed the maximum working pressure of the cylinders, even temporarily.

- When the cylinders have been filled securely and the process is completed, immediately remove the cylinders and the equipment from the site and close all isolation valves on the equipment.

- The recovered refrigerant should not be re-used in any other refrigeration system unless it has been cleaned and checked.

R290 System Service

When repairing systems that use R290 refrigerant, the following warnings and operating requirements should be noted.

Warning about the R290 refrigerant

The following information indicates a hazard with a medium level of risk which, if not avoided, could result in death or serious injury.

The following applies to R290 refrigerant systems.

Prior to beginning work on systems containing flammable refrigerants, safety checks are necessary to ensure that the risk of ignition is minimized.

For repair to the refrigerating system, the following precautions shall be complied with prior to conducting work on the system.

Work shall be undertaken under a controlled procedure so as to minimize the risk of a flammable gas or vapour being present while the work is being performed.

All maintenance staff and others working in the local area shall be instructed on the nature of work being carried out. Work in confined spaces shall be avoided. The area around the workspace shall be sectioned off. Ensure that the conditions within the area have been made safe by control of flammable material.

The area shall be checked with an appropriate refrigerant detector prior to and during work, to ensure the technician is aware of potentially flammable atmospheres.

Ensure that the leak detection equipment being used is suitable for use with flammable refrigerants, i.e. non-sparking, adequately sealed or intrinsically safe.

If any hot work is to be conducted on the refrigeration equipment or any associated parts, appropriate fire extinguishing equipment shall be available to hand. Have a dry powder or CO2 fire extinguisher adjacent to the charging area.

No person carrying out work in relation to a refrigeration system which involves exposing any pipe work that contains or has contained flammable refrigerant shall use any sources of ignition in such a manner that it may lead to the risk of fire or explosion.

All possible ignition sources, including cigarette smoking, should be kept sufficiently far away from the site of installation, repairing, removing and disposal, during which flammable refrigerant can possibly be released to the surrounding space.

Prior to work taking place, the area around the equipment is to be surveyed to make sure that there are no flammable hazards or ignition risks. “No Smoking” signs shall be displayed.

Ensure that the area is in the open or that it is adequately ventilated before breaking into the system or conducting any hot work. A degree of ventilation shall continue during the period that the work is carried out. The ventilation should safely disperse any released refrigerant and preferably expel it externally into the atmosphere.

Where electrical components are being changed, they shall be fit for the purpose and to the correct specification. At all times the manufacturer’s maintenance and service guidelines shall be followed. If in doubt consult the manufacturer’s technical department for assistance.

The following checks shall be applied to installations using flammable refrigerants:

–	The charge size is in accordance with the room size within which the refrigerant containing parts are installed;

–	The ventilation machinery and outlets are operating adequately and are not obstructed;

–	If an indirect refrigerating circuit is being used, the secondary circuit shall be checked for the presence of refrigerant;

–	Marking to the equipment continues to be visible and legible. Markings and signs that are illegible shall be corrected;

–	refrigeration pipe or components are installed in a position where they are unlikely to be exposed to any substance which may corrode refrigerant containing components, unless the components are constructed of materials which are inherently resistant to being corroded or are suitably protected against being so corroded.

Repair and maintenance to electrical components shall include initial safety checks and component inspection procedures.

If a fault exists that could compromise safety, then no electrical supply shall be connected to the circuit until it is satisfactorily dealt with. If the fault cannot be corrected immediately but it is necessary to continue operation, an adequate temporary solution shall be used. This shall be reported to the owner of the equipment so all parties are advised.

Initial safety checks shall include:

-that capacitors are discharged: this shall be done in a safe manner to avoid possibility of sparking;

-that no live electrical components and wiring are exposed while charging, recovering or purging the system;

-that there is continuity of earth bonding.

During repairs to sealed components, all electrical supplies shall be disconnected from the equipment being worked upon prior to any removal of sealed covers, etc. If it is absolutely necessary to have an electrical supply to equipment during servicing, then a permanently operating form of leak detection shall be located at the most critical point to warn of a potentially hazardous situation.

Particular attention shall be paid to the following to ensure that by working on electrical components, the casing is not altered in such a way that the level of protection is affected. This shall include damage to cables, excessive number of connections, terminals not made to original specification, damage to seals, incorrect fitting of glands, etc.

Ensure that seals or sealing materials have not degraded such that they no longer serve the purpose of preventing the ingress of flammable atmospheres.

Replacement parts shall be in accordance with the manufacturer’s specifications.

Do not apply any permanent inductive or capacitance loads to the circuit without ensuring that this will not exceed the permissible voltage and current permitted for the equipment in use.

Intrinsically safe components are the only types that can be worked on while live in the presence of a flammable atmosphere. The test apparatus shall be at the correct rating.

Replace components only with parts specified by the manufacturer. Other parts may result in the ignition of refrigerant in the atmosphere from a leak.

Check that cabling will not be subject to wear, corrosion, excessive pressure, vibration, sharp edges or any other adverse environmental effects. The check shall also take into account the effects of ageing or continual vibration from sources such as compressors or fans.

When breaking into the refrigerant circuit to make repairs – or for any other purpose – conventional procedures shall be used. However, it is important that best practice is followed.

Since flammability is a consideration. The following procedure shall be adhered to:

•	Remove refrigerant.

•	Purge the circuit with inert gas.

•	Evacuate.

•	Purge again with inert gas.

•	Open the circuit by cutting or brazing.

The refrigerant charge shall be recovered into the correct recovery cylinders. The system shall be “flushed” with OFN to render the unit safe. This process may need to be repeated several times. Compressed air or oxygen shall not be used for this task.

Flushing shall be achieved by breaking the vacuum in the system with OFN and continuing to fill until the working pressure is achieved, then venting to atmosphere, and finally pulling down to a vacuum.

This process shall be repeated until no refrigerant is within the system. When the final OFN charge is used, the system shall be vented down to atmospheric pressure to enable work to take place.

This operation is absolutely vital if brazing operations on the pipe-work are to take place.

Ensure that the outlet for the vacuum pump is not close to any ignition sources and there is ventilation available. Ensure that contamination of different refrigerants does not occur when using charging equipment. Hoses or lines shall be as short as possible to minimize the amount of refrigerant contained in them. Prior to recharging the system it shall be pressure tested with OFN.

DD.12 Decommissioning:

Before carrying out this procedure, it is essential that the technician is completely familiar with the equipment and all its detail. It is recommended good practice that all refrigerants are recovered safely. Prior to the task being carried out, an oil and refrigerant sample shall be taken in case analysis is required prior to re-use of reclaimed refrigerant. It is essential that electrical power is available before the task is commenced.

a)	Become familiar with the equipment and its operation.

b)	Isolate system electrically.

c)	Before attempting the procedure ensure that:

•	Mechanical handling equipment is available, if required, for handling refrigerant cylinders.

•	All personal protective equipment is available and being used correctly.

•	The recovery process is supervised at all times by a competent person.

•	Recovery equipment and cylinders conform to the appropriate standards.

d)	Pump down refrigerant system, if possible.

e)	If a vacuum is not possible, make a manifold so that refrigerant can be removed from various parts of the system.

f)	Make sure that cylinder is situated on the scales before recovery takes place.

g)	Start the recovery machine and operate in accordance with manufacturer's instructions.

h)	Do not overfill cylinders. (No more than 80 % volume liquid charge).

i)	Do not exceed the maximum working pressure of the cylinder, even temporarily.

j)	When the cylinders have been filled correctly and the process completed, make sure that the cylinders and the equipment are removed from site promptly and all isolation valves on the equipment are closed off.

k)	Recovered refrigerant shall not be charged into another refrigeration system unless it has been cleaned and checked.

Equipment shall be labelled stating that it has been de-commissioned and emptied of refrigerant. The label shall be dated and signed. Ensure that there are labels on the equipment stating the equipment contains flammable refrigerant.

When removing refrigerant from a system, either for servicing or decommissioning, it is recommended good practice that all refrigerants are removed safely.

When transferring refrigerant into cylinders, ensure that only appropriate refrigerant recovery cylinders are employed. Ensure that the correct number of cylinders for holding the total system charge are available. All cylinders to be used are designated for the recovered refrigerant and labelled for that refrigerant (i.e. special cylinders for the recovery of refrigerant). Cylinders shall be complete with pressure relief valve and associated shut-off valves in good working order. Empty recovery cylinders are evacuated and, if possible, cooled before recovery occurs.

The recovery equipment shall be in good working order with a set of instructions concerning the equipment that is at hand and shall be suitable for the recovery of flammable refrigerants. In addition, a set of calibrated weighing scales shall be available and in good working order. Hoses shall be complete with leak-free disconnect couplings and in good condition. Before using the recovery machine, check that it is in satisfactory working order, has been properly maintained and that any associated electrical components are sealed to prevent ignition in the event of a refrigerant release. Consult manufacturer if in doubt.

The recovered refrigerant shall be returned to the refrigerant supplier in the correct recovery cylinder, and the relevant Waste Transfer Note arranged. Do not mix refrigerants in recovery units and especially not in cylinders.

If compressors or compressor oils are to be removed, ensure that they have been evacuated to an acceptable level to make certain that flammable refrigerant does not remain within the lubricant. The evacuation process shall be carried out prior to returning the compressor to the suppliers. Only electric heating to the compressor body shall be employed to accelerate this process. When oil is drained from a system, it shall be carried out safely.

Warning: disconnect the appliance from its power source during service and when replacing parts.

These units are partial unit air conditioners, complying with partial unit requirements of this International Standard, and must only be connected to other units that have been confirmed as complying to corresponding partial unit requirements of this International Standard.

Qualification requirements for maintenance personnel

The following information indicates a hazard with a high level of risk which, if not avoided, will result in death or serious injury.

These instructions are exclusively intended for qualified contractors and authorized installers

Work on the refrigerant circuit with flammable refrigerant in safety group A3 may only be carried out by authorized heating contractors. These heating contractors must be trained in accordance with EN 378 Part 4 or IEC 60335-2-40, Section HH. The certificate of competence from an industry accredited body.

Brazing/soldering work on the refrigerant circuit may only be carried out by contractors certified in accordance with ISO 13585 and AD 2000, Datasheet HP 100R. And only by contractors qualified and certified for the processes to be carried out. The work must fall within the range of applications purchased and be carried out in accordance with the prescribed procedures. Soldering/brazing work on accumulator connections requires certification of personnel and processes by a notified body according to the Pressure Equipment Directive (2014/68/EU).

Work on electrical equipment may only be carried out by a qualified electrician.

Before initial commissioning, all safety relevant points must be checked by the particular certified heating contractors. The system must be commissioned by the system installer or a qualified person authorized by the installer.

Electric wiring diagram

Electric Control Box Layout

Low voltage box

|  |  |  | Main Control PCB |
| --- | --- | --- | --- |
| Power supply terminals | Wire clip | Reserve strong current control port | Communication terminals block |

High voltage box

| Filter PCB | Reactor |  |
| --- | --- | --- |
|  |  | Fan inverter PCB |
| Fuse PCB | Compressor & fan inverter PCB |  |

Outdoor Unit PCBs

Main Control PCB

| Label | Code | Port | Content | Rated Voltage |
| --- | --- | --- | --- | --- |
| 1 | CN34 | T3 | Port for T3 temp. sensor | DC 3.3 V |
| 2 | CN45 | T4 | Port for T4 temp. sensor | DC 3.3 V |
| 3 | CN7 | TL | Port for TL temp. sensor | DC 3.3 V |
| 4 | CN5 | Th | Port for Th temp. sensor | DC 3.3 V |
| 5 | CN50 | Tp | Port for Tp temp. sensor | DC 3.3 V |
| 6 | CN47 | T2B/T2 | Port for T2&T2B temp. sensor | DC 5 V |
| 7 | CN10 | Tw_out / Tw_in | Port for Two & Twi temp. sensor | DC 5 V |
| 8 | CN39 | T1 | Port for T1 temp. sensor | DC 5 V |
| 9 | CN8 | FS | Port for water switch | DC 12 V |
| 10 | CN20 | FM | Reserved | DC 5 V |
| 11 | CN37 | PW | Port for temperature sensor of water pressure | DC 5 V |
| 12 | CN24 | Tbt | Port for Tbt temp. sensor | DC 5 V |
| 13 | CN13 | T5/T1B | Port for T5/T1B temp. sensor | DC 5 V |
| 14 | CN17 | PUMP_BP | Port for internal pump | / |
| 15 | CN38 | T52 | Port for T52 temp. sensor | DC 5 V |
| 16 | CN15 | Tw2 | Port for Tw2 temp. sensor | DC 5 V |
| 17 | CN18 | Tsolar | Port for Tsolar temp. sensor | DC 5 V |
| 18 | CN66 | S2 S1 K2 K1 | switch input K1/K2,solar energy input S1/S2 | DC 5 V |
| 19 | CN31 | CL COM HT 0 -10V | Output port for 0-10V(0-10V)Control port for room thermostat (heating mode)(HT) /Power port for room thermostat(COM)/Control port for room thermostat (cooling mode)(CL) | DC 5 V |
| 20 | CN36 | 12V T1 T2 GND | Port for thermostat transfer board | DC 12 V |
| 21 | CN63 | SG EVU | Port for smart grid (photovoltaic signal)(SG)/Port for smart grid (grid signal)(EVU) | DC 12 V |
| 22 | CN61 | M1 M2 | Port for remote switch | DC 12 V |
| 23 | CN9 | IB IA GND IBH2 IBH1 | Control port for internal backup heater1/2 (reserved) | / |
| 24 | CN30 | A B X/HA Y/HB E T1 T2 E1 H1 H2 | Port for communication with the wired controller(Port,3,4),Port for thermostat transfer board (Port 6.7) ，Port for Internal machine Parallel(Port 8,9,10) | AB: DC 12 V X/HA Y/HB: DC 18 V T1 T2 E1 H1 H2: DC 5 V |
| 25 | SW9 | SW9 | Dip switch | DC 5 V |
| 26 | S3 | S3 | Dip switch | DC 5 V |
| 27 | S2 | S2 | Dip switch | DC 5 V |
| 28 | S1 | S1 | Dip switch | DC 5 V |
| 29 | CN11 | / | Additional heat source(Port1,2)，Port for SV1(3-way valve)( Port3,4)，，Port for SV2(3-way valve)( Port5,6)，Port for SV3(3-way valve)( Port7,8)，Port for zone 2 pump(P_c)/ zone 1 pump(P_o)/ solar energy pump(P_s)/ pipe pump(P_d)(Port9,10,11,12)，Control port for tank booster heater (Port13)，Control port for internal backup heater 1（Port14），Control port for internal backup heater 2（Port15），Reserved(Port24) | AC 230 V |
| 30 | CN22 | N IBH1 BH2 TBH | Control port for backup heater/booster heater | AC 230 V |
| 31 | CN32 | AC OUT | Port for transformer power input | AC 230 V |
| 32 | CN42 | HEAT6 | Port for anti-freeze electric heating tape | AC 230 V |
| 33 | CN29 | HEAT5 | Port for anti-freeze electric heating tape | AC 230 V |
| 34 | CN41 | HEAT1 | Reserved | AC 230 V |
| 35 | CN40 | OUT1 | Reserved | AC 230 V |
| 36 | CN62 | HEAT3 | Port for anti-freeze electric heating tape | DC 12 V |
| 37 | CN71 | ST1 | Port for four-way valve | AC 230 V |
| 38 | CN56 | SV6 | Port for the heating tape of drainage outlet | AC 230 V |
| 39 | CN68 | HEAT4 | Port for the heating tape of drainage outlet | AC 230 V |
| 40 | CN28 | PUMP | Port for the water pump | AC 230 V |
| 41 | CN21 | POWER | Port for power supply | AC 230 V |
| 42 | S4 | S4 | Dip switch | DC 3.3 V |
| 43 | S5 | S5 | Dip switch | DC 3.3 V |
| 44 | S6 | S6 | Dip switch | DC 3.3 V |
| 45 | CN27 | EEV3 | Port for electrical expansion valve 3 | DC 12 V |
| 46 | CN44 | EEV2 | Port for electrical expansion valve 2 | DC 12 V |
| 47 | CN33 | EEV1 | Port for electrical expansion valve 1 | DC 12 V |
| 48 | CT2 | CN2 | Port for power supply monitor | DC 3.3 V |
| 49 | CT1 | CN49 | Port for power supply monitor | DC 3.3 V |
| 50 | CN16 | T9I/T9O | Port for T9I/T9O temp. sensor | DC 3.3 V |
| 51 | CN46 | L-SEN | Port for low pressure sensor | DC 5 V |
| 52 | CN3 | H-SEN | Port for high pressure sensor | DC 5 V |
| 53 | CN43 | COMM | Port for communication with Inverter module | DC 5 V |
| 54 | CN35 | RS485, on/off | Reserved | DC 5 V |

Compressor & fan inverter PCB

| Label | Code | Port | Content | Voltage |
| --- | --- | --- | --- | --- |
| 1 | CN38 | P N | DC fan power output port | DC 565 V |
| 2 | CN26 | 19V GND | Fan module board power supply port | DC 19 V |
| 3 | CN3 | UVW | Port output for fan | Phase to phase voltage AC 46-460 V |
| 4 | CN8 | O-Motor | PTC relay control port/communication port | DC 12 V / DC 5 V |
| 5 | CN9 | O-Motor | PTC relay control port/communication port | DC 12 V / DC 5 V |
| 6 | CN25 | / | / | / |
| 7 | CN27 | / | PED board socket | / |
| 8 | S7 | / | Module address DIP switch | / |
| 9 | CN21 | H-Pro | High pressure switch | / |
| 10 | CN19 | W | Power output for compressor | Phase to phase voltage AC 46-460 V |
| 11 | CN18 | V |  | Phase to phase voltage AC 46-460 V |
| 12 | CN17 | U |  | Phase to phase voltage AC 46-460 V |
| 13 | CN15 | L3 | Power input port | Phase to phase voltage AC 380V |
| 14 | CN7 | L2 |  | Phase to phase voltage AC 380V |
| 15 | CN16 | L1 |  | Phase to phase voltage AC 380V |
| 16 | CN5 | P-out | Output for reactor | / |
| 17 | CN1 | P-in | Input from reactor | / |

Fan inverter PCB

| Label | Code | Port | Content | Voltage |
| --- | --- | --- | --- | --- |
| 1 | CN7 | / | Port for power supply | DC 565 V |
| 2 | CN4 | / | Fan module communication port | DC 5 V |
| 3 | CN1 | / | Fan module communication port | DC 5 V |
| 4 | CN2 | / | EEPROM programming port | DC 5 V |
| 5 | CN6 | / | Port for fan inverter PCB power supply | DC 19 V |
| 6 | CN9 | DEBUG | Programming port | DC 5 V |
| 7 | CN3 | U V W | DC fan power ports | Phase to phase voltage AC 46-460 V |

Filter PCB

| Label | Code | Port | Content | Voltage |
| --- | --- | --- | --- | --- |
| 1 | CN4 | L1 | Power input L1 | AC 380-415 V |
| 2 | CN3 | L2 | Power input L2 |  |
| 3 | CN2 | L3 | Power input L3 |  |
| 4 | CN1 | N | Reserved | / |
| 5 | CN15 | L1L2L3 | Reserved | AC 380-415 V |
| 6 | CN11 | N A B C | Reserved | AC 380-415 V |
| 7 | CN6 | L3’ | Output power L3' | AC 380-415 V |
| 8 | CN7 | L2' | Output power L2' |  |
| 9 | CN8 | L1' | Output power L1' |  |

Fuse PCB

| Label | Code | Port | Content | Voltage |
| --- | --- | --- | --- | --- |
| 1 | CN12 | / | Fuse 1-1 | AC 230 V |
| 2 | CN15 | L3' | Input power L3' | AC 230 V |
| 3 | CN11 | / | Fuse 2-1 | AC 230 V |
| 4 | CN14 | L2' | Input power L2' | AC 230 V |
| 5 | CN13 | L1' | Input power L1' | AC 230 V |
| 6 | CN10 | / | Fuse 3-1 | AC 230 V |
| 7 | CN4 | / | Fuse 3-2 | AC 230 V |
| 8 | CN1 | L1 | Output power L1 | AC 230 V |
| 9 | CN2 | L2 | Output power L2 | AC 230 V |
| 10 | CN5 | / | Fuse 2-2 | AC 230 V |
| 11 | CN3 | L3 | Output power L3 | AC 230 V |
| 12 | CN6 | / | Fuse 1-2 | AC 230 V |

Digital Display Output

| Digital display output in different operating states |  |
| --- | --- |
| Outdoor unit state | Parameters displayed on Main Control PCB DSP1 |  |  |
| On standby | 0 |  |  |
| Normal operation | The current frequency of compressor |  |  |
| Error or protection | Error or protection code |  |  |

Cascade setting and Modbus function

The DIP switch S3 on Main Control PCB is used for setting the Modbus address. By defaulting the units have this DIP switch positioned=0/0/0

| Dip switch |  |
| --- | --- |
| Dip switch ON=1 OFF=0; Factory settings. S3; 1/2/3; 0/0/0=address 0#(master unit) 1/0/0=address 1#(slave unit) 0/1/0=address 2#(slave unit) 0/0/1=address 3#(slave unit) 1/1/0=address 4#(slave unit) 1/0/1=address 5#(slave unit); 1:OFF 2:OFF 3:OFF. 4; Reserved; 4:OFF. |
| Cascade and Modbus Connection |  |
| Modbus Wiring |  |

DIP Switch Settings

DIP switch S1, S2, S3, S4, S5 and S6 are located on the main control PCB Keep factory Settings.

Point check button

Point check button SW1 and SW2 are located on the main control PCB.

Point check button is for the use of research and development personnel, and should not be touched under normal circumstances.

Error Code Table

| Water circuit error |  |  |  |
| --- | --- | --- | --- |
| Error code | Description | Displayed on |  |
| E0 | water flow failure (10 times of E8) | User Interface and Main Control PCB |  |
| E8 | water flow protection | User Interface and Main Control PCB |  |
| Communication error |  |  |  |
| Error code | Description | Displayed on |  |
| E2 | Communication fault between User Interface and Main Control PCB | User Interface and Main Control PCB |  |
| H0 | Communication error of Main Control PCB | User Interface and Main Control PCB |  |
| H1 | Communication error between Main Control PCB and inverter PCB | User Interface and Main Control PCB |  |
| Hd | Communication fault between master unit and slave unit. | User Interface and Main Control PCB |  |
| Sensor error |  |  |  |
| Error code | Description | Displayed on |  |
| E3 | T1 Electric Heater/AHS water outlet temperature sensor error | User Interface and Main Control PCB |  |
| E4 | T5 Water tank temperature sensor error | User Interface and Main Control PCB |  |
| E5 | T3 Outdoor unit heat exchanger bottom temperature sensor error | User Interface and Main Control PCB |  |
| E6 | T4 Ambient temperature sensor error | User Interface and Main Control PCB |  |
| E7 | Tbt Balance tank temperature sensor/ Final outlet water temperature of cascade system sensor error | User Interface and Main Control PCB |  |
| E9 | Th Return-air temperature sensor error | User Interface and Main Control PCB |  |
| EA | Tp Discharge temperature sensor error | User Interface and Main Control PCB |  |
| Eb | Tsolar Solar panel temperature sensor error | User Interface and Main Control PCB |  |
| EC | T5_2 Water tank temperature sensor error (Reserved) | User Interface and Main Control PCB |  |
| Ed | Tw_in Plate heat exchanger inlet water temperature sensor error | User Interface and Main Control PCB |  |
| FC1 | TL Outdoor unit heat exchanger outlet temperature sensor error | User Interface and Main Control PCB |  |
| H2 | T2 Plate heat exchanger outlet refrigerant temperature sensor error | User Interface and Main Control PCB |  |
| H3 | T2B Plate heat exchanger inlet refrigerant temperature sensor error | User Interface and Main Control PCB |  |
| H5 | Ta room temperature sensor error | User Interface and Main Control PCB |  |
| H8 | H-SEN High-pressure sensor error | User Interface and Main Control PCB |  |
| H9 | Tw2 Zone 2 water flow temperature sensor error | User Interface and Main Control PCB |  |
| HA | Tw_out Plate heat exchanger outlet water temperature sensor error | User Interface and Main Control PCB |  |
| P21 | L-SEN Low-pressure sensor error | User Interface and Main Control PCB |  |
| P27 | H-SEN and L-SEN connected reversely (Detect when compressor is off) | User Interface and Main Control PCB |  |
| F51 | Temperature sensor(T9I) fault | User Interface and Main Control PCB |  |
| F31 | Temperature sensor(T9O) fault | User Interface and Main Control PCB |  |
| F6 | EXV1 fault | User Interface and Main Control PCB |  |
| F61 | EXV2 fault | User Interface and Main Control PCB |  |
| F62 | EXV3 fault | User Interface and Main Control PCB |  |

| Voltage error |  |  |  |
| --- | --- | --- | --- |
| Error code | Description | Displayed on |  |
| E1 | Phase loss or phase reversal. | User Interface and Main Control PCB | For 3Ph units |
| H7 | Power overvoltage and Power under voltage protection | User Interface and Main Control PCB |  |
| FE | Lack of L2 phase fault. | User Interface and Main Control PCB |  |
| Protection code |  |  |  |
| Error code | Description | Displayed on |  |
| P0 | Low-pressure protection | User Interface and Main Control PCB |  |
| P1 | High-pressure switch protection | User Interface and Main Control PCB |  |
| P3 | Overcurrent protection | User Interface and Main Control PCB |  |
| P4 | Compressor protection against excessively-high discharge temperature | User Interface and Main Control PCB |  |
| Pd | Protection for over-high condensing temperature in cooling mode | User Interface and Main Control PCB |  |
| HP | Low-pressure protection in cooling mode | User Interface and Main Control PCB |  |
| bA | T4 sensor out of operation range protection | User Interface and Main Control PCB |  |
| PP | Protection for abnormal temperature difference between outlet water and inlet water | User Interface and Main Control PCB |  |
| Hb | PP occurs 3 times in heating/DHW mode | User Interface and Main Control PCB |  |
| P5 | The big temperature difference between outlet water temp. and inlet water temp. | User Interface and Main Control PCB |  |
| Inverter module error/ protection |  |  |  |
| Error code | Description | Displayed on |  |
| C7 | Over-high temperature protection for IPM module | User Interface and Main Control PCB |  |
| H4 | 3 times of “L1*” in 60 minutes | User Interface and Main Control PCB |  |
| L1E | Hardware overcurrent protection | Main Control PCB |  |
| L11 | Phase current instantaneous overcurrent protection | Main Control PCB |  |
| L12 | Phase current continuous 30s overcurrent protection | Main Control PCB |  |
| L2E | Over-temperature protection | Main Control PCB |  |
| L3E | Bus voltage too low error | Main Control PCB |  |
| L31 | Bus voltage too high error | Main Control PCB |  |
| L32 | Bus voltage excessively high error | Main Control PCB |  |
| L34 | Phase loss error of three-phase power supply | Main Control PCB | For 3Ph units |
| L35 | L2 phase mismatch fault | Main Control PCB | For 3Ph units |
| L43 | Abnormal phase current sampling bias | Main Control PCB |  |
| L45 | Fan motor code mismatch error | Main Control PCB |  |
| L46 | IPM protection (FO) | Main Control PCB |  |
| L47 | Module type mismatch | Main Control PCB |  |
| L5E | Motor failed to start | Main Control PCB |  |
| L52 | Motor stalling protection | Main Control PCB |  |
| L6E | Phase loss protection | Main Control PCB |  |
| L61 | compressor terminals short circuit protection | Main Control PCB |  |
| L65 | IPM short circuit protection | Main Control PCB |  |
| LBE | Action of high-pressure switch | Main Control PCB |  |
| LB7 | PED bH error | Main Control PCB |  |
| H6 | Fan 1 failure | User Interface and Main Control PCB |  |
| H61 | Fan 2 failure | User Interface and Main Control PCB |  |
| HH | 10 times of H6 / H61 in 120min | User Interface and Main Control PCB |  |
| J1E | Hardware overcurrent protection | Main Control PCB |  |
| J11 | Phase current instantaneous overcurrent protection | Main Control PCB |  |
| J12 | Phase current continuous 30s overcurrent protection | Main Control PCB |  |
| J2E | Over-temperature protection | Main Control PCB |  |
| J3E | Bus voltage too low error | Main Control PCB |  |
| J31 | Bus voltage too high error | Main Control PCB |  |
| J32 | Bus voltage excessively high error | Main Control PCB |  |
| J43 | Abnormal phase current sampling bias | Main Control PCB |  |
| J45 | Fan motor code mismatch error | Main Control PCB |  |
| J46 | IPM Protection (FO) | Main Control PCB |  |
| J47 | Module type mismatch (after module resistance tested) | Main Control PCB |  |
| J5E | Motor failed to start | Main Control PCB |  |
| J52 | Motor stalling protection | Main Control PCB |  |
| J6E | Phase loss protection | Main Control PCB |  |
| J61 | Fan terminals short circuit protection | Main Control PCB |  |
| J65 | IPM short circuit protection | Main Control PCB |  |
| HF | Drive does not match model | User Interface and Main Control PCB |  |
| Others |  |  |  |
| Error code | Description | Displayed on |  |
| Pb | Pb is the indicator that shows the system is running in anti-freezing control | Main Control PCB |  |

Troubleshooting

Warning

- All electrical work must be carried out by competent and suitably qualified, certified and accredited professionals and in accordance with all applicable legislation (all national, local and other laws, standards, codes, rules, regulations and other legislation that apply in a given situation).

- Power-off the outdoor units before connecting or disconnecting any connections or wiring, otherwise electric shock (which can cause physical injury or death) may occur or damage to components may occur.

WARNING!

E0, E8 Troubleshooting

Digital display output

Description

| Error code |  | E0 | E8 |
| --- | --- | --- | --- |
| Description |  | water flow failure | water flow protection |
| Triggering |  | 5 times of No-water detection failures in a row before pump on Or 10 times of E8 in a row when do running-water detection after pump on | No-water detection failures before pump on or water flow switch breaks after pump on within 10 times |
| Relative ports and Locations | CN28 PUMP (To supply power for water pump) |  |  |
|  | CN17 PUMP BP (feedback signal of water pump) |  |  |
|  | CN8 FS (signal of water flow switch) |  |  |
|  | Layout of main component | Code; Code; Code; Code. 1; Automatic air purge valve; 7; Flow switch. 2; Backup heater; 8; Pump. 3; Expansion vessel; 9; Plate heat exchanger. 4; Refrigerant gas pipe; 10; Water outlet pipe. 5; Temperature sensor; 11; Pressure relief valve. 6; Refrigerant liquid pipe; 12; Water inlet pipe. |
| User Interface |  | E0 (** %) / E8 (** %) is displayed on the User Interface. The percentage indicates possible cause of water flow failure, which is illustrated as note 1. |  |
| Correct Dip switch |  |  |  |

Procedure

| E0 / E8: Water flow failure |  |  |
| --- | --- | --- |
| No water flow before the pump starts. Yes | No | Turn off other pump that out of the unit before the pump starts within the unit.. |
| Check the error code E0(**%) /E8(**%) displayed on the User Interface, and the percentage is between 5%-80% | No | Check the details of Note 1 |
| Yes |  |  |
| Check the water pump indicator lights, and it shows water pump is normal (SHIMGE water pump 5 lights all on indicates normal) | No | Check the details of Note 2 |
| Yes |  |  |
| Check the water circuit, and it is abnormal: 1. The ball valve which is connected to the unit is not opened 2. Water inlet and outlet pipe connected reversely. 3.Y-type filter is dirty block 4.The power cable(CN28) or feedback signal cable(CN17) is not connected properly 5. The water circuit was not filled first and not released air completely. | Yes | 1. Open the waterway ball valve which is connected to the unit 2. Make sure water inlet and outlet pipe connected correctly. 3. Clean the filter. 4. Connect the power cable or feedback signal cable correctly. 5. Fill the water circuit first and then release the air. If necessary, we can quickly release the air from the air purge valve by unscrewing black nut. |
| No |  |  |
| Check the Water flow switch, and it is damaged 1. Flow switch FS plug (CN8) is not connected properly. 2. The water flow in the pipe is not consistent with arrow on the flow switch. 3. Remove the water flow switch from the pipeline, manually dial the water flow switch rake to closed status, and use a digital multimeter with buzzer to measure. If it does not beep, the water flow switch damaged. | Yes | 1.Insert the plug of the water flow switch correctly 2. Adjust the direction of water flow in the pipe to be the same as the arrow on the flow switch 3. When you manually dial the water flow switch to the closed status, use a digital multimeter with buzzer to measure. If buzzer sounds, the water flow switch is normal. Otherwise, it’s damaged and replace with a new water flow switch. |
| No |  |  |
| For more error information of water pump and flow switch, check the note 3/4 to solve the problem. If the error still occurs, request aftersales service |  |  |

Note 1:

| The meaning of percentage of water pump output(displayed on the user interface) |  |  |  |
| --- | --- | --- | --- |
| Percentage | Water pump model | Brand | Description |
| 0-70% | APF25-12-130E FPWM1 | SHIMGE | Pump works normally, feedbacks 0-4.0m³/h flow information (Q=0.057PWMout, Q: m3/h, PWMout: %) |
| 85% | APF25-12-130E FPWM1 | SHIMGE | Alarm（Undervoltage＜160V or Phase loss or Overcurrent or Overheat）, and pump stops running |
| 90% | APF25-12-130E FPWM1 | SHIMGE | Alarm（Motor stalling protection）, and pump stops running |
| 95% | APF25-12-130E FPWM1 | SHIMGE | Pump Standby |

Note 2 – Indicator lights on SHIMGE water pump :

| Indicator lights on SHIMGE water pump |  |  |
| --- | --- | --- |
| Name | Indicator lights | Description |
| Motor stalling protection |  | When the electric pump rotor shaft is stuck, the electric pump displays a fault code, feedback 90% positive duty cycle and attempts to restart. It restarts every 1 second and stops after restarting 255 times. |
| Phase loss protection |  | When the electric pump phase failure occurs, the electric pump displays a fault code, feedback 85% positive duty cycle and attempts to restart. It restarts every 1 second and stops after restarting 255 times. |
| Overcurrent protection |  | When a short-circuit fault occurs in the electric pump, the electric pump is shut down for protection, feedback is 85% positive duty cycle, the panel displays a fault code, and the machine shuts down without restarting. |
| Overheat protection |  | When the power module overheats, the electric pump shuts down for protection, feedback 85% positive duty cycle, the panel displays a fault code, and shuts down for protection. |
| Undervoltage protection |  | When the input voltage is less than 160V, the electric pump shuts down for protection, feedback 85% positive duty cycle, the panel displays a fault code, and shuts down for protection. |

Note 3: The possible error and solutions of water pump

| The possible causes of water pump failure and solutions |  |  |
| --- | --- | --- |
| Description | Possible cause | Solution |
| Error occurs at the first time running | Water pump leak | Replace the sealing ring |
|  | Water inlet and outlet pipe connected reversely. | Connect the pipe correctly. |
|  | The power cable (CN28) is not connected properly | Connect the power cable correctly. |
|  | The feedback signal cable (CN17) is not connected properly | Connect the feedback signal cable correctly. |
|  | The dip switch is not correct. | Correct the dip switch as the illustration above |
| Error occurs at the first time running or after running for a while | Pump idling | Fill the water circuit first and then release the air |
|  | Pump stalling | Remove the water pump, Rotate the impeller manually until it can move freely. And then install it back. (If it’s too hard to rotate the impeller manually, replace the water pump) |
|  | Power supply is abnormal | Check the power supply |
| Error occurs after running for a while | E8 occurs after water pump running for a while | Fill the water circuit first and then release the air. |
| Error occurs at the first time running or after running for a while | Motor stall, and it can not be rotated manually | Replace water pump |
| Error occurs at the first time running | Water pump connection is correct, the water pump icon on the User Interface is lit, while no indicator lights on water pump is lit. | Replace water pump |

E2 Troubleshooting

Digital display output

Description

| Error code |  | E2 |
| --- | --- | --- |
| Description |  | Communication fault between User Interface and Main Control PCB |
| Triggering |  | Main Control PCB side: Communication failure with User Interface lasts 2 min Or User Interface side: No communication reply from Main Control PCB for 1 min |
| Relative ports and Locations | X/HA、Y/HB |  |

Procedure

| E2: Communication fault between User Interface and the unit |  |  |
| --- | --- | --- |
| Communication cables from port X/HA, Y/HB was disconnected, or misconnected | Yes | Reconnect the communication cables securely |
| No |  |  |
| Communication cables from port X/HA, Y/HB have short circuited or damaged | Yes | Replace the communication cables |
| No |  |  |
| Replace a new User Interface, and the error code still displays | Yes | Replace the Main Control PCB |
| No |  |  |
| Back to normal |  |  |

H0 Troubleshooting

Digital display output

Description

| Error code | H0 |
| --- | --- |
| Description | Communication error of Main Control PCB |
| Triggering | Communication failure lasts 1 min |

Procedure

| H0: Communication error of Main Control PCB |  |  |
| --- | --- | --- |
| Replace the Main Control PCB |  |  |

H1 Troubleshooting

Digital display output

Description

| Error code |  | H1 |
| --- | --- | --- |
| Description |  | Communication error between Main Control PCB and Compressor & Fan Inverter PCB |
| Triggering |  | Check the communication after power-on 1 min. If no communication is detected, the error is triggered |
| Relative ports and locations | LED3 & CN43 COMM (Main Control PCB) |  |
|  | LED3 & BUS voltage(P-in/N) (Compressor & Fan Inverter PCB) |  |

Procedure

For 3Ph models

| H1：Communication error between Main Control PCB and Compressor & Fan Inverter PCB |  |  |  |  |
| --- | --- | --- | --- | --- |
| 1. Check whether power supply for ODU is abnormal.( The normal range is around 342-456V) 2. Check whether there is loss of L1, L2, or L3 | Yes | 1.Adjust power supply 2.Connect L1,L2,L3 correctly and firmly |  |  |
| NO Check whether the LED3 on Main Control PCB is off. NO | Yes | Measure the voltage of the first and fourth pin of CN43 on Main Control PCB, which is not around 5VDC | Yes | If yes, replace the Main Control PCB |
| Check whether the LED3 on Compressor & Fan Inverter PCB is off Or The bus voltage between P-in, N < 540VDC | Yes | Measure the voltage of the fifth and sixth pin of CN43 on Main Control PCB, which is not around 12VDC | Yes | If yes, replace the Main Control PCB If no, replace the inverter control box |
| No |  |  |  |  |
| Check whether the cable between the Main Control PCB and Compressor & Fan Inverter PCB is abnormal (The cable from CN43) | Yes | Make sure the cable is connected correctly. Replace a new cable if necessary. |  |  |
| No |  |  |  |  |
| Replace the Main Control PCB first, if error still occurs, replace the Compressor & Fan Inverter PCB |  |  |  |  |

Hd Troubleshooting

Digital display output

Description

| Error code |  | Hd |
| --- | --- | --- |
| Description |  | Communication fault between master unit and slave unit. |
| Triggering |  | For cascade system, the communication failure between master unit and slave unit lasts 2min and above |
| Relative ports and locations | Communication port E1/H1/H2 |  |
|  | Dip switch S3-1/2/3 0/0/0=address 0#（Master） 1/0/0=address 1#（Slave） 0/1/0=address 2#（Slave） 0/0/1=address 3#（Slave） 1/1/0=address 4#（Slave） 1/0/1=address 5#（Slave） |  |
|  | SW9 0/0= default setting |  |

Procedure

| Hd：The communication fault between master unit and slave unit. |  |  |
| --- | --- | --- |
| Check “Unit Status-Operation parameter-Online unit number” on the User Interface, and the number is consistent with the actual unit number |  |  |
| No |  |  |
| Communication cables between port H1H2E1 was disconnected, or misconnected | Yes | Reconnect the communication cables securely |
| No |  |  |
| Communication cables between port H1H2E1 have short circuited or damaged | Yes | Replace the communication cables |
| No |  |  |
| 1. Confirm Dip switch S3-1/2/3 of each unit, Ensure it’s all correct and not repeated. 2. Confirm SW9 of master unit is 1/1 | No | Reset the S3 and SW9, power off and re-power again |
| Yes |  |  |
| The time difference of providing power supply time for master unit and slave unit is greater than 1 min | Yes | Make sure the time difference of providing power supply for master unit and slave unit is within 1 min |
| No |  |  |
| Replace Main Control PCB of the unit whose Hd still occurs |  |  |

E5, E6, E9, EA, FC1, H2, H3, F51, F31, F6, F61, F62 Troubleshooting

Digital display output

Description

| Code | Description | Port | Locations |
| --- | --- | --- | --- |
| E5 | T3 Outdoor unit heat exchanger bottom temperature sensor error | CN34 |  |
| E6 | T4 Ambient temperature sensor error | CN45 |  |
| E9 | Th Return-air temperature sensor error | CN5 |  |
| EA | Tp Discharge temperature sensor error | CN50 |  |
| FC1 | TL Outdoor unit heat exchanger outlet temperature sensor error | CN7 |  |
| H2 | T2 Plate heat exchanger outlet refrigerant temperature sensor error | CN47 |  |
| H3 | T2B Plate heat exchanger inlet refrigerant temperature sensor error |  |  |
| F51 | Temperature sensor(T9O) fault | CN16 |  |
| F31 | Temperature sensor(T9I) fault |  |  |
| F6 | EXV1 fault | CN33 |  |
| F61 | EXV2 fault | CN44 |  |
| F62 | EXV3 fault | CN27 |  |

Procedure

| E5, E6, E9, EA, FC1, H2, H3, F51,F31 ,F6,F61,F62：Temperature sensor error |  |  |
| --- | --- | --- |
| Temperature sensor connection on Main Control PCB is loose, misconnected, broken or moisten | Yes | Reconnect the temperature sensor correctly and keep it dry |
| No |  |  |
| Pull out temperature sensor, measure sensor resistance: If the resistance is too low(< 0.5 kΩ), the sensor has short-circuited. If the resistance is too high(>380kΩ) , the sensor has failed. You can also measure the resistance and compare it with sensor’s resistance characteristics table (Refer to Appendix to part 4) If the resistance is not consistent, the sensor has failed.（except for F6,F61,F62） | Yes | Replace the sensor and it will be back to normal automatically |
| No |  |  |
| Check the fixed position of the sensor, and the sensor probe falls off | Yes | Re-fix the sensor firmly to the installation position |
| No |  |  |
| Replace Main Control PCB |  |  |

E3, E4, E7, Eb, EC, Ed, HA, H9 Troubleshooting

Digital display output

Description

| Code | Description | Port | Location (Main Control PCB) |  |
| --- | --- | --- | --- | --- |
| E3 | T1 Electric Heater/AHS water outlet temperature sensor error | CN39 |  |  |
| E4 | T5 Water tank temperature sensor error | CN13 |  |  |
| E7 | Tbt1 Balance tank temperature sensor/ Final outlet water temperature of cascade system sensor error | CN24 |  |  |
| Eb | Tsolar Solar panel temperature sensor error | CN18 |  |  |
| EC | T5_2 Water tank temperature sensor error (Reserved) | CN38 |  |  |
| Ed | Tw_in Plate heat exchanger inlet water temperature sensor error | CN10 |  |  |
| HA | Tw_out Plate heat exchanger outlet water temperature sensor error |  |  |  |
| H9 | Tw2 Zone 2 water flow temperature sensor error | CN15 |  |  |

Note 1: Dip switch settings or User Interface settings

| Code | Description |
| --- | --- |
| Ed | Main Control PCB can not detect the right sensor value. |
| HA |  |
| E3 | IBH function is on (Dip switch S1-3/4 is set IBH available, and User Interface- For Serviceman - Other heat source – IBH function=1), while Main Control PCB can not detect the right T1 sensor value. AHS function is on (User Interface- For Serviceman - Other heat source - AHS function=1), while Main Control PCB can not detect the right T1 sensor value. |
| E4 | DHW mode is on (User Interface- For Serviceman – DHW setting- DHW mode=1), while Main Control PCB can not detect the right T5 sensor value. |
| E7 | Tbt is on (User Interface- For Serviceman- Input definition- Tbt=1), while Main Control PCB can not detect the right Tbt sensor value. |
| Eb | Solar function is on and Solar control is on (User Interface- For Serviceman - Other heat source - Solar function=1 & Solar control=1), while Main Control PCB can not detect the right Tsolar sensor value. |
| EC | T5_2 is on (User Interface- For Serviceman- Input definition- Tbt=1), while Main Control PCB can not detect the right T5_2 sensor value. (Reserved) |
| H9 | Double zone is on (User Interface- For Serviceman –Temp. type setting – Double zone=1), while Main Control PCB can not detect the right Tw2 sensor value. |

Procedure

| E3, E4, E7, Eb, EC, H9: Temperature sensor error |  |  |
| --- | --- | --- |
| Check the Dip switch settings or User Interface settings as illustrated above | No | Reset dip switch, and reboot the unit, make sure parameter are set available |
| Yes |  |  |
| Temperature sensor connection on Main Control PCB is loose, misconnected, broken or moisten | Yes | Reconnect the temperature sensor correctly and keep it dry |
| No |  |  |
| Pull out temperature sensor, measure sensor resistance: If the resistance is too low(< 0.5 kΩ), the sensor has short-circuited. If the resistance is too high(>950kΩ) , the sensor has failed. You can also measure the resistance and compare it with sensor’s resistance characteristics table (Refer to Appendix to part 4) , If the resistance is not consistent, the sensor has failed. | Yes | Replace the sensor and it will be back to normal automatically |
| No |  |  |
| Check the fixed position of the sensor, and the sensor probe falls off | Yes | Re-fix the sensor firmly to the installation position |
| No |  |  |
| Replace Main Control PCB |  |  |

H5 Troubleshooting

Digital display output

Description

| Code | Description | Locations |
| --- | --- | --- |
| H5 | Ta room temperature sensor error | Inserted on User Interface PCB |

Procedure

| H5：Ta Temperature sensor error |  |  |
| --- | --- | --- |
| Replace User Interface |  |  |

H8, P21, P27 Troubleshooting

Digital display output

Description

| Code | Description | Port | Location(Main Control PCB) |
| --- | --- | --- | --- |
| H8 | H-SEN High pressure sensor error | CN3 |  |
| P21 | L-SEN Low pressure sensor error | CN46 |  |
| P27 | H-SEN and L-SEN connected reversely (Detect when compressor is off) | CN3/CN46 |  |

Procedure

| H8, P21: Pressure sensor error |  |  |
| --- | --- | --- |
| Temperature sensor connection on Main Control PCB is loose, misconnected, broken or moisten | Yes | Reconnect the temperature sensor correctly and keep it dry |
| No |  |  |
| Measure the resistance value of sensor, and it’s consistant with the curve (refter to appedix to Part 4 - Temperature Sensor Resistance Characteristics) | Yes | Replace Main Control PCB |
| No |  |  |
| Replace pressure sensor |  |  |

| P27: Pressure sensor error |  |  |
| --- | --- | --- |
| Make sure high pressure sensor connected to H-SEN(CN3), and low pressure sensor connected to L-SEN(CN46) |  |  |

E1 Troubleshooting

Digital display output

Description

| Error code |  | E1 (For 3Ph models) |
| --- | --- | --- |
| Description |  | Phase loss or phase reversal |
| Triggering |  | At least one of L1/L2/L3/N misconnected or disconnected |
| Relative ports and locations | Terminal blocks |  |

Procedure

| E1: Phase loss or phase reversal |  |  |
| --- | --- | --- |
| Power off the unit, and check L1/L2/L3/N on terminal block for any misconnections or disconnections. | Yes | Ensure L1/L2/L3/N is securely connected and the phase sequence is correct |
| No |  |  |
| Replace the Compressor & Fan Inverter PCB |  |  |
| No |  |  |
| Replace the Main Control PCB |  |  |

H7 Troubleshooting

Digital display output

Description

| Error code | H7 |
| --- | --- |
| Description | Power overvoltage and Power undervoltage protection |
| Triggering | Input voltage≤172V or Input voltage≥265V (The unit will back to normal if input voltage≥180V or input voltage ≤250V) |

Procedure

| H7: Power overvoltage and power undervoltage protection |  |  |
| --- | --- | --- |
| H7 occurs when powered off Or H7 occurs when powered on immediately after powering off, display for 5min and then disappears | Yes | The system is protection enabled and no action is required. |
| No |  |  |
| Measure the input voltage on terminal blocks, it’s too high(≥265V) or too low(≤172V) | Yes | Adjust the input power supply |
| No |  |  |
| Determine possible inverter PCB failure (Refer to part 4 Appendix: Guide for identifying inverter PCB failure) | Yes | Replace the Compressor & Fan Inverter PCB |
| No |  |  |
| Request aftersales service |  |  |

FE Troubleshooting

Digital display output

Description

| Error code | FE |
| --- | --- |
| Description | Lack of L2 phase fault |
| Triggering | Input voltage≤150V (The unit will back to normal if input voltage≥160V) |

Procedure

| FE: Lack of L2 phase fault |  |  |
| --- | --- | --- |
| Power off the unit，and check if L2 on the wiring board is disconnected | Yes | Make sure L2 is well connected |
| No |  |  |
| Measure the input voltage on terminal blocks, it’s too low(≤150V) | Yes | Adjust the input power supply |
| No |  |  |
| Replace the Main Control PCB |  |  |

P0 Troubleshooting

Digital display output

Description

| Error code | P0 |
| --- | --- |
| Description | Low-pressure protection |
| Triggering | 1、The Main Control PCB detected that the low pressure was < 0.12Mpa and lasts 30 min 2、The Main Control PCB detected that the low pressure was < 0.13Mpa and lasts 5 seconds ,and compressor stopped running and lasts 2 min at the same time. 3、The Main Control PCB detected that the low pressure was < 0.13Mpa and lasts 5 seconds, and compressor is already running and lasts, and T4<-10℃，and the unit is in running except defrost and forced cooling operation. |
| H-SEN and L-SEN Locations |  |

Procedure

| P0: Low pressure protection |  |  |
| --- | --- | --- |
| Check “Unit Status-Operation parameter-P1 comp. pressure & P2 comp. pressure” on the User Interface when the unit stops running, and P1=P2 | No | Replace low pressure sensor |
| Yes T4 sensor fell out from the fixed position or was contact with something in high temperature.. No Use a digital multimeter to measure the resistance and comprare it with sensor’s resistance characteristics table (Refer to Appendix to part 4), If the resistance is not consistent, the sensor has failed.. No | Yes Yes | Re-fix the T4 sensor to the installation position.. Replace the T4 temperature sensor. |
| The unit was installed in a site that is narrow, with bad ventilation, or with thick snow or ice. Or the heat exchanger was blocked. | Yes | Place the unit somewhere broad, with good ventilation, or without thick snow or ice. Make sure the heat exchanger be not blocked. |
| No |  |  |
| Check whether the finned tube heat exchanger is dirty block | Yes | Clean the finned tube heat exchanger |
| No |  |  |
| Reboot the unit, observe whether the fan is running normally | No | Replace fan motor or identify whether Compressor & Fan Inverter PCB failed (Refer to Appendix to part 4: Guide for identifying Compressor & Fan Inverter PCB failure) |
| Yes Check “Unit Status-Operation parameter-P1 comp. pressure” on the User Interface, Compare it with the reference value in Discharge / Suction pressure and temperature range in appedix 4, and the parameter on the User Interface is lower than the one in appedix 4. No | Yes | Refrigerant leakage. Please contact professionals to identify the leak position, vacuum and refill the refrigerant according to the nameplate.. |
| Reboot the unit, hold the electronic expansion valve coil to feel whether it is working, and listen the “Click” sound when the valve turn on/off. | Yes | Check for blockages between the electronic expansion valve and Copper filter. Re-clean the unit, and recharge the refrigerant by serviceman with refrigeration expertise |
| No |  |  |
| Request aftersales service |  |  |

P1 Troubleshooting

Digital display output

Description

| Error code | P1 |
| --- | --- |
| Description | High pressure switch protection |
| Triggering | The Main Control PCB detected that the high pressure was ≥ 3.5 Mpa |
| High pressure switch location | The location of high pressure switch refer to Part 2 Component Layout and Refrigerant Circuits |
| High pressure switch plug |  |
| Make sure water pressure and water flow rate is in the proper range | The proper water pressure range:(0.3bar-3bar) The proper water flow rate range Unit; Flow rate range (m3/h). 26 kW; 1.2-5.4. 30 kW; 1.2-6.2. 35 kW; 1.2-7.2. 40 kW; 1.2-8.1. |

Procedure

| P1 occurs in Cooling mode |  |  |
| --- | --- | --- |
| High pressure switch connection on the inverter control PCB is loose, misconnected | Yes | Reconnect high pressure switch correctly |
| No |  |  |
| Power on and back to normal | No | Use a digital multimeter to measure high pressure switch and the inverter control PCB with buzzer. If no buzzer sounds, high pressure switch or the inverter control PCB is damaged, replace high pressure switch or the inverter control box that damaged. |
| Yes |  |  |
| Reboot the unit and check “Unit Status-Operation parameter-P1 comp. pressure” on the User Interface. Confirm P1 comp. pressure >3.5MPa when the P1 error occurred. | No | Replace the high pressure switch |
| Yes |  |  |
| The unit was installed in a site that is narrow, with bad ventilation, or in a high temperature. Or the heat exchanger was blocked. | Yes | Place the unit somewhere broad, with good ventilation, or in a medium temperature. Make sure the heat exchanger be not blocked. |
| No |  |  |
| Check whether the finned tube heat exchanger is dirty block | Yes | Clean the finned tube heat exchanger |
| No |  |  |
| Reboot the unit, observe whether the fan is running normally | No | Replace fan motor or identify whether Compressor & Fan Inverter PCB failed (Refer to Appendix to part 4: Guide for identifying Compressor & Fan Inverter PCB failure) |
| Yes |  |  |
| Reboot the unit, hold the electronic expansion valve coil to feel whether it is working, and listen the “Click” sound when the valve turn on/off. | Yes | Re-clean the unit, and recharge the refrigerant by serviceman with refrigeration expertise |
| No |  |  |
| Request aftersales service |  |  |

| P1 occurs in Heating/DHW mode |  |  |
| --- | --- | --- |
| Check “Unit Status-Error info.” on the User Interface, and E8/E0/P5 code also occured barely at the same time | Yes | Check and clean pipe and filter, make sure water pressure and water flow rate is in the proper range as above. For more details, refer to E8/E0/P5 troubleshooting procedure. |
| No |  |  |
| High pressure switch connection on the inverter control PCB is loose, misconnected | Yes | Reconnect high pressure switch correctly |
| No |  |  |
| Power off and power on again , back to normal | No | Use a digital multimeter to measure high pressure switch and the inverter control PCB with buzzer. If no buzzer sounds, high pressure switch or the inverter control PCB is damaged, replace high pressure switch or the inverter control box that damaged. |
| Yes |  |  |
| Check “Unit Status-Operation Parameter-Twout/Twin” on the User Interface,and the temperature difference between Twout and Twin is large | Yes | Check and clean pipe and filter, make sure water pressure and water flow rate is in the proper range as above. |
| No |  |  |
| Reboot the unit and check “Unit Status-Operation parameter-P1 comp. pressure” on the User Interface. Confirm P1 comp. pressure >3.5MPa when the P1 error occurred. | No | Replace the high pressure switch |
| Yes |  |  |
| Reboot the unit, hold the electronic expansion valve coil to feel whether it is working, and listen the “Click” sound when the valve turn on/off. | Yes | Re-clean the unit, and recharge the refrigerant by serviceman with refrigeration expertise |
| No |  |  |
| Replace the inverter control box |  |  |

| P1 occurs in Off status |  |  |
| --- | --- | --- |
| Check “Unit Status-Operation parameter-P1 comp. pressure & P2 comp. pressure” on the User Interface, and P1&P2<3.5MPa | No | Request aftersales service |
| Yes |  |  |
| Check whether high pressure switch plug was disconnected, or misconnected | Yes | Re-connect the high pressure witch plug |
| No |  |  |
| Measure the high pressure switch to check whether it keeps closed | Yes | Replace high pressure switch |

P3 Troubleshooting

Digital display output

Description

| Error code | P3 |
| --- | --- |
| Description | Overcurrent protection |
| Triggering | The Main Control PCB detected that the input current is higher than protection value |
| Teminal block |  |

Procedure

| P3 occurs in heating / DHW mode |  |  |
| --- | --- | --- |
| Measure the input voltage of terminal block, and it’s<198V | Yes | Adjust the power supply based on the rated voltage range |
| No |  |  |
| Use a current clamp to measure the current of power cables connected to L on terminal block, compare it with “Unit Status-Operation parameter-ODU current” on the User Interface, and the difference> ¦1.5A¦ | Yes | Replace the inverter control box |
| No |  |  |
| Check “Unit Status-Error info.” on the User Interface, and E8/E0 code also occur barely at the same time | Yes | Check and clean pipe and filter, make sure water pressure and water flow rate is in the proper range For more details, refer to E8/E0 troubleshooting procedure. |
| No |  |  |
| Reboot the unit, hold the electronic expansion valve coil to feel whether it is working, and listen the “Click” sound when the valve turn on/off. | No | Request aftersales service |
| Yes |  |  |
| Power off the unit, confirm whether compressor cables were disconnected, or misconnected | Yes | Reconnect the compressor cables correctly |
| No |  |  |
| Use a digital multimeter to measure the resistance between each two of compressor terminals. The resistance <10 Ohm or the resistance=0(Short circuited) | Yes | Replace the compressor |
| No |  |  |
| Power off the unit, and identify whether Compressor & Fan Inverter PCB failed. (Refer to Appendix to part 4: Guide for identifying Compressor & Fan Inverter PCB failure) | Yes | Replace the inverter control box |
| No |  |  |
| Reboot the unit, and the error still occurs | No | Back to normal |
| Yes |  |  |
| Adjust compressor cables, make sure U, V, W are connected to the corresponding position, then reboot the unit. | Yes | Replace the inverter control box |
| No |  |  |
| Replace the compressor |  |  |

| P3 occurs in cooling mode |  |  |
| --- | --- | --- |
| Measure the input voltage of terminal block, and it’s<198V | Yes | Adjust the power supply based on the rated voltage range |
| No |  |  |
| Use a current clamp to measure the current of power cables connected to L on terminal block, compare it with “Unit Status-Operation parameter-ODU current” on the User Interface, and the difference> ¦1.5A¦ | Yes | Replace the inverter control box |
| No |  |  |
| The unit was installed in a site that is narrow, with bad ventilation, or in a high temperature. Or the heat exchanger was blocked. | Yes | Place the unit somewhere broad, with good ventilation, or in a medium temperature. Make sure the heat exchanger be not blocked. |
| No |  |  |
| Check whether the finned tube heat exchanger is dirty block | Yes | Clean the finned tube heat exchanger |
| No |  |  |
| Reboot the unit, observe whether the fan is running normally | No | Replace fan motor or identify whether Compressor & Fan Inverter PCB failed (Refer to Appendix to part 4: Guide for identifying Compressor & Fan Inverter PCB failure) |
| Yes |  |  |
| Reboot the unit, hold the electronic expansion valve coil to feel whether it is working, and listen the “Click” sound when the valve turn on/off. | No | Request aftersales service |
| Yes |  |  |
| Re-clean the unit, and recharge the refrigerant by serviceman with refrigeration expertise.Then Reboot the unit, and the error still occurs | No | Back to normal |
| Yes |  |  |

| Power off the unit, confirm whether compressor cables were disconnected, or misconnected | Yes | Reconnect the compressor cables correctly |
| --- | --- | --- |
| No |  |  |
| Use a digital multimeter to measure the resistance between each two of compressor terminals. The resistance <10 Ohm or the resistance=0 (Short circuited) | Yes | Replace the compressor |
| No |  |  |
| Power off the unit, and identify whether Compressor & Fan Inverter PCB failed. (Refer to Appendix to part 4: Guide for identifying Compressor & Fan Inverter PCB failure) | Yes | Replace the inverter control box |
| No |  |  |
| Reboot the unit, and the error still occurs | No | Back to normal |
| Yes |  |  |
| Adjust compressor cables, make sure U, V, W are connected to the corresponding position, then reboot the unit. | Yes | Replace the inverter control box |
| No |  |  |
| Replace the compressor |  |  |

P4 Troubleshooting

Digital display output

Description

| Error code |  | P4 |
| --- | --- | --- |
| Description |  | The protection for overheat discharge temperature of Compressor |
| Triggering |  | The Main Control PCB detected that the compressor discharge temperature was ≥115℃ |
| Relative ports and locations | Tp | You can find Tp sensor by the sensor cable from Tp port |
|  | Tw_in Tw_out |  |

Procedure

| P4 |  |  |
| --- | --- | --- |
| Pull out Tp temperature sensor from compressor fixed sleeve, leave it in the air for 10 min, if the temperature difference between sensor and air is greater than 5℃, the sensor failed. You can also measure the resistance and compare it with sensor’s resistance characteristics table (Refer to Appendix to part 4) , If the resistance is not consistent, the sensor has failed. | Yes | Replace Tp temperature sensor |
| No |  |  |
| Check whether Tw_out / Tw_in sensor felt out from installation port | Yes | Install the Tw_in / Tw_out sensor back to the installation port, so they can detect the actual temperature. |
| No |  |  |
| Pull out Tw_out / Tw_in sensor from plate heat exchanger ,leave it in the air for 10 min, if the temperature difference between sensor and air is greater than 5℃, the sensor failed. You can also measure the resistance and compare it with sensor’s resistance characteristics table (Refer to Appendix to part 4). If the resistance is not consistent, the sensor has failed. | Yes | Replace Tw_out / Tw_in temperature sensor |
| No |  |  |
| Check “Unit Status-Operation parameter-P2 comp. pressure” on the User Interface, Compare it with the reference value in Discharge / Suction pressure and temperature range in appedix 4, and the parameter on the User Interface is lower than the one in appedix 4 | Yes | Refrigerant leakage. Please contact professionals to identify the leak position, vacuum and refill the refrigerant according to the nameplate. |
| No |  |  |
| Request aftersales service |  |  |

Pd Troubleshooting

Digital display output

Description

| Error code | Pd |
| --- | --- |
| Description | The protection for overheat condensing temperature |
| Triggering | The Main Control PCB detected that it’s in cooling mode and the condensing temperature was ≥65℃ |
| Relative ports and locations |  |

Procedure

| Pd: The protection for overheat condensing temperature in cooling mode |  |  |
| --- | --- | --- |
| Check “Unit Status-Operation parameter-P1 comp. pressure & P2 comp. pressure” on the User Interface when the unit stops running, and P1=P2 | No | Replace the Main Control PCB or high pressure sensor.（Refer to section 6.10.3:H8/P21 troubleshooting procedure） |
| Yes |  |  |
| The unit was installed in a site that is narrow, with bad ventilation, or in a high temperature. Or the heat exchanger was blocked. | Yes | Place the unit somewhere broad, with good ventilation, or in a medium temperature. Make sure the heat exchanger be not blocked. |
| No |  |  |
| Check whether the finned tube heat exchanger is dirty block | Yes | Clean the finned tube heat exchanger |
| No |  |  |
| Reboot the unit, observe whether the fan is running normally | No | Replace fan motor or identify whether Compressor & Fan Inverter PCB failed (Refer to Appendix to part 4: Guide for identifying Compressor & Fan Inverter PCB failure) |
| Yes |  |  |
| Reboot the unit, hold the electronic expansion valve coil to feel whether it is working, and listen the “Click” sound when the valve turn on/off. | Yes | Check for blockages between the electronic expansion valve and Copper filter. Re-clean the unit, and recharge the refrigerant by serviceman with refrigeration expertise |
| No |  |  |
| Request aftersales service |  |  |

HP Troubleshooting

Digital display output

Description

| Error code | HP |
| --- | --- |
| Description | Low pressure protection in cooling mode |
| Triggering | The Main Control PCB detected that the suction pressure P2<0.35Mpa for 5 seconds in cooling mode and compressor running over 300 seconds. |
| Tw_in Tw_out |  |

Procedure

| HP: Low pressure protection in cooling mode |  |  |
| --- | --- | --- |
| Check whether Tw_out sensor felt out from installation port | Yes | Install the Tw_out sensor back to the installation port, so they can detect the actual temperature. |
| No |  |  |
| Pull out Tw_out / Tw_in sensor from plate heat exchanger, leave it in the air for 10 min, if the temperature difference between sensor and air is greater than 5℃, the sensor failed. You can also measure the resistance and comprare it with sensor’s resistance characteristics table (Refer to Appendix to part 4). If the resistance is not consistent, the sensor has failed. | Yes | Replace Tw_out/Tw_in temperature sensor |
| No |  |  |
| Check Unit Status-Operation parameter-P1 comp. pressure & P2 comp. pressure” on the User Interface when the unit stops running, and P1=P2 | No | Replace L-SEN low pressure sensor |
| Yes |  |  |
| Check “Unit Status-Operation parameter-P1 comp. pressure” on the User Interface, Compare it with the reference value in Discharge / Suction pressure and temperature range in appedix 4, and the parameter on the User Interface is lower than the one in appedix 4 | Yes | Refrigerant leakage. Please contact professionals to identify the leak position, vacuum and refill the refrigerant according to the nameplate. |
| No |  |  |
| Reboot the unit, hold the electronic expansion valve coil to feel whether it is working, and listen the “Click” sound when the valve turn on/off. | Yes | Check for blockages between the electronic expansion valve and Copper filter. Re-clean the unit, and recharge the refrigerant by serviceman with refrigeration expertise. |
| No |  |  |
| Request aftersales service |  |  |

bA Troubleshooting

Digital display output

Description

| Error code | bA |
| --- | --- |
| Description | T4 sensor out of operation range protection |
| Triggering | In heating/ DHW mode, the error occurs when T4≥65℃ or T4<-25℃ In cooling mode, the error occurs when T4≥65℃ or T4<-5℃ |
| T4 |  |

Procedure

| bA: T4 sensor out of operation range protection |  |  |
| --- | --- | --- |
| The actual ambient temperature ≥65℃ or <-25℃ in heating mode; or the actual ambient temperature≥65℃ or <-5℃ in cooling mode | Yes | The actual ambient temperature is out of range, so Protection program activated. No action required. |
| No |  |  |
| T4 sensor fell out from the fixed position or was contact with something in high/low temperature. | Yes | Re-fix the T4 sensor to the installation position. |
| No |  |  |
| The outdoor unit was in a high temperature place or exposed to sunlight | Yes | Move the outdoor unit to a ventilation place far away from the high temperature heat source and do a good job of shading treatment. |
| No |  |  |
| Take out T4 sensor from the fixed position, hold it in hand in 5 min. Check “Unit Status-Operation parameter-T4 outdoor air temp.” on the User Interface, and it’s close to body temperature. | Yes | The actual ambient temperature is out of range, so Protection program activated. No action required. |
| No |  |  |
| Replace the T4 sensor |  |  |

PP, Hb Troubleshooting

Digital display output

Description

| Error code | PP | Hb |
| --- | --- | --- |
| Description | The protection for abnormal temperature difference between outlet water and inlet water | 3 times of PP in heating/DHW mode |
| Triggering | Twout-Twin≥3℃ and lasts 15 min in cooling mode Twin-Twout≥3℃ and lasts 15 min in heating/DHW mode | 3 times of PP in heating/DHW mode; When Twout<7℃ occurs, the number of PP failures increases by one |
| Outlet pipe and inlet pipe |  |  |
| Tw_in Tw_out |  |  |
| CN71 ST1 Port for 4-way valve |  |  |
| For-way valve E S C |  |  |

Procedure

| PP in cooling mode |  |  |
| --- | --- | --- |
| Outlet pipe and inlet pipe connected reversely | Yes | Re-connect the pipes securely |
| No |  |  |
| Tw_in sensor and Tw_out sensor connected reversely on plate heat exchanger or on Main control PCB | Yes | Re-connect the sensors securely |
| No |  |  |
| Pull out Tw_out/Tw_in sensor from plate heat exchanger, leave it in the air for 10 min, if the temperature difference between sensor and air is greater than 5℃, the sensor failed. You can also measure the resistance and compare it with sensor’s resistance characteristics table (Refer to part 4 Appendix), If the resistance is not consistent, the sensor has failed. | Yes | Replace Tw_out / Tw_in temperature sensor |
| No |  |  |
| Connection cable of 4-way valve was disconnected, or misconnected | Yes | Re-connect the cable securely |
| No |  |  |
| Measure the voltage of port for 4-way valve, and it’s 200-240V | No | Replace the Main Control PCB |
| Yes |  |  |
| Feel the temperature of the 4- way valve by hand, C pipe is hot, E pipe is cold | Yes | Replace 4-way valve |
| No |  |  |
| Request aftersales service |  |  |

| PP/Hb in heating/DHW mode |  |  |
| --- | --- | --- |
| Outlet pipe and inlet pipe connected reversely | Yes | Re-connect the pipes securely |
| No |  |  |
| Tw_in sensor and Tw_out sensor connected reversely on plate heat exchanger or on Main control PCB | Yes | Re-connect the sensors securely |
| No |  |  |
| Pull out Tw_out / Tw_in sensor from plate heat exchanger, leave it in the air for 10 min, if the temperature difference between sensor and air is greater than 5℃, the sensor failed. You can also measure the resistance and compare it with sensor’s resistance characteristics table (Refer to part 4 Appendix), If the resistance is not consistent, the sensor has failed. | Yes | Replace Tw_out / Tw_in temperature sensor |
| No |  |  |
| Connection cable of 4-way valve was misconnected | Yes | Re-connect the cable securely |
| No |  |  |
| Feel the temperature of the 4- way valve by hand, C pipe is hot, E pipe is cold | No | Replace 4-way valve |
| Yes |  |
| Request aftersales service |

P5 Troubleshooting

Digital display output

Description

| Error code | P5 |
| --- | --- |
| Description | The big temperature difference between outlet water temp. and inlet water temp. |
| Triggering | Twout-Twin≥30℃ in heating/DHW mode Twout-Twin≥17℃ in cooling mode |

Procedure

| P5：The big temperature difference between outlet water temp. and inlet water temp. |  |  |
| --- | --- | --- |
| Check Unit Status-Error info. on the User Interface, and E8/E0 code occurred at roughly the same time | Yes | Check and clean pipe and filter, Ensure water pressure and water-flow rate is in Proper range For more details, refer to E8/E0 troubleshooting procedure. |
| No |  |  |
| Check Unit Status-Operation Parameter-water flow” is smaller than normal | Yes | Check and clean pipe and filter, Ensure water pressure and water-flow rate is in Proper range |
| No |  |  |
| Check whether Twout/Twin sensor fell out from the fixed position | Yes | Re-fix the Twout /T win sensor to the installation position. |
| No |  |  |
| Pull out Tw_out / Tw_in sensor from plate heat exchanger, leave it in the air for 10 min, if the temperature difference between sensor and air is greater than 5℃, the sensor failed. You can also measure the resistance and compare it with sensor’s resistance characteristics table (Refer to part 4 Appendix), If the resistance is not consistent, the sensor has failed. | Yes | Replace Tw_out / Tw_in temperature sensor |
| No |  |  |
| Whether the heating water temperature rises rapidly, the cooling water temperature drops rapidly and the unit stops quickly. You can Check the temperature by “Unit Status-Operation parameter-Tw_in plate water inlet temp. and Tw_out plate water outlet temp.” on the User Interface | Yes | Re-select a model of proper capacity |
| No |  |  |
| The heat pump runs in DHW mode | Yes | The heat exchange area of the coil in the water tank is too small, replace the water tank with larger heat exchange coil. The heat exchanger coil of the tank is ≥1.05 m². |
| No |  |  |
| Increase the buffer tank according to the selection requirements, increase the water capacity of the system and reduce the water side resistance. |  |  |

C7 Troubleshooting

Description

| Error code | C7 |
| --- | --- |
| Description | Overheat temperature protection for IPM module |
| Triggering | IPM module temperature ≥ 95℃ |

Digital display output

Procedure

| C7：Overheat temperature protection for IPM module |  |  |
| --- | --- | --- |
| Check whether the software version of the inverter control box is correct. Yes | No | Upgrade correct software. |
| The unit was installed in a site that is narrow, with bad ventilation, or in a high temperature. Or the heat exchanger was blocked. | Yes | Place the unit somewhere broad, with good ventilation, or in a medium temperature. Make sure the heat exchanger be not blocked. |
| No |  |  |
| Check whether the finned tube heat exchanger is dirty block | Yes | Clean the finned tube heat exchanger |
| No |  |  |
| Check whether the inverter control box is dirty block or with some obstacles | Yes | Remove the obstacle |
| No |  |  |
| Reboot the unit, observe whether the fan is running normally | No | Replace fan motor or identify whether Compressor & Fan Inverter PCB failed (Refer to Appendix to part 4: Guide for identifying Compressor & Fan Inverter PCB failure) |
| Yes |  |  |
| Request aftersales service |  |  |

H4, L** Troubleshooting

Digital display output

Description

| Error code | Description | Note |
| --- | --- | --- |
| H4 | 3 times of “L1*” in 60 min |  |
| L** | Inverter module protection | Check the specific code on digital display panel on the Main Control PCB |

The specific L** code table:

| Error code | Description | Note |
| --- | --- | --- |
| L1E | Hardware overcurrent protection |  |
| L11 | Phase current instantaneous overcurrent protection |  |
| L12 | Phase current continuous 30s overcurrent protection |  |
| L2E | Over-temperature protection |  |
| L3E | Bus voltage too low error |  |
| L31 | Bus voltage too high error |  |
| L32 | Bus voltage excessively high error |  |
| L34 | Phase loss error of three-phase power supply | For 3Ph models |
| L43 | Abnormal phase current sampling bias |  |
| L45 | Fan motor code mismatch error |  |
| L46 | IPM protection (FO) |  |
| L47 | Module type mismatch |  |
| L5E | Motor failed to start |  |
| L52 | Motor stalling protection |  |
| L6E | Phase loss protection |  |
| L61 | Compressor terminals short circuit protection |  |
| L65 | IPM short circuit protection |  |
| LBE | Action of high pressure switch |  |
| LB7 | PED bH error |  |

Procedure

| H4, L**: Inverter module protection |  |  |
| --- | --- | --- |
| Check whether the software version of the Compressor & Fan Inverter PCB is correct. Yes | No | Upgrade correct software. |
| Power off the unit, the compressor connection cables was disconnected, or misconnected | Yes | Reconnect the cables correctly |
| No |  |  |
| Use a digital multimeter to measure the resistance between each two of compressor terminals. If the resistance <10 Ohm, compressor failed | Yes | Replace the compressor |
| No |  |  |
| Power off the unit, and identify whether Compressor & Fan Inverter PCB failed. (Refer to Appendix to part 4: Guide for identifying Compressor & Fan Inverter PCB failure) | Yes | Replace the inverter control box |
| No |  |  |
| Reboot the unit, error still occurs | No | Back to normal |
| Yes |  |  |
| Replace the compressor, and reboot the unit again, while error still occurs | Yes | Replace the Compressor & Fan Inverter PCB |
| No |  |  |
| Back to normal |  |  |

- H6, H61 HH, J** Troubleshooting

Digital display output

Description

| Error code | Description | Note |
| --- | --- | --- |
| H6 / H61 | Fan failure | / |
| HH | 10 times of H6 / H61 in 120min | / |
| J** | Fan module failure | Check the specific code on digital display panel on the Main Control PCB |

The specific J** code table:

| Error code | Description |
| --- | --- |
| J1E | Hardware overcurrent protection |
| J11 | Phase current instantaneous overcurrent protection |
| J12 | Phase current continuous 30s overcurrent protection |
| J2E | Over-temperature protection |
| J3E | Bus voltage too low error |
| J31 | Bus voltage too high error |
| J32 | Bus voltage excessively high error |
| J43 | Abnormal phase current sampling bias |
| J45 | Fan motor code mismatch error |
| J46 | IPM protection (FO) |
| J47 | Module type mismatch (after module resistance tested) |
| J5E | Motor failed to start |
| J52 | Motor stalling protection |
| J6E | Phase loss protection |
| J61 | Fan terminals short circuit protection |
| J65 | IPM short circuit protection |

Procedure

| H6,H61, HH，J**: Fan failure |  |  |
| --- | --- | --- |
| Power off the unit, the fan connection cables was disconnected, or misconnected | Yes | Reconnect the cables correctly |
| No |  |  |
| Use a digital multimeter to measure the resistance between each two of fan terminals. If the resistance <10 Ohm, fan motor failed | Yes | Replace the fan |
| No |  |  |
| Power off the unit, and identify whether Compressor & Fan Inverter PCB or Fan Inverter PCB failed. (Refer to Appendix to part 4: Guide for identifying Compressor & Fan Inverter PCB or Fan Inverter PCB failure) | Yes | Replace the Compressor & Fan Inverter PCB or Fan Inverter PCB |
| No |  |  |
| Reboot the unit, error still occurs | No | Back to normal |
| Yes |  |  |
| Replace the fan motor, and reboot the unit again, while error still occurs | Yes | Compressor & Fan Inverter PCB or Fan Inverter PCB |
| No |  |  |
| Back to normal |  |  |

HF Troubleshooting

Digital display output

Description

| Error code |  | HF |
| --- | --- | --- |
| Description |  | Drive does not match model |
| Triggering |  | The driving program of Compressor & Fan Inverter PCB is detected as being mismatched with Dip switch |
| Relative ports and locations | Dip switch S5 S6 |  |
| Correct Dip switch | S5 | Mars series:0/0/0/0 |
|  | S6 |  |

Procedure

| HF：Outdoor unit EEPROM error |  |  |
| --- | --- | --- |
| Set the Dip switch to the correct position, and re-power the unit after 20s, the error still displays | No | Back to normal |
| Yes |  |  |
| Replace Main Control PCB | No | Back to normal |
| Yes |  |  |
| Replace the Compressor & Fan Inverter PCB |  |  |

Pb Troubleshooting

Digital display output

Description

| Error code | Pb |
| --- | --- |
| Description | Pb is the indicator that shows the system is running in anti-freezing control |
| Triggering | Refer to Part 3 - Protection control – Anti-freezing protection control |
| User Interface | It shows anti-freezing icon on the User Interface |

Discharge / Suction pressure and temperature range

The following parameter ranges are used to roughly determine whether the system is running properly:

| Discharge temperature (Tp) on heating/DHW mode |  |
| --- | --- |
| T4＜-10℃ | Twout+10＜Tp＜Twout+30 |
| -10℃≤T4＜10℃ | Twout+10＜Tp＜Twout+30 |
| 10℃≤T4＜25℃ | Twout+10＜Tp＜Twout+25 |
| T4≥25℃ | Twout+10＜Tp＜Twout+25 |
| Note: T4: ambient temperature Tw_out: leaving water temperature. |  |

| Discharge temperature (Tp) on cooling mode |  |  |  |  |
| --- | --- | --- | --- | --- |
| Tp Value (℃) | Fx＜44Hz | 44Hz≤Fx＜62Hz | 62Hz≤Fx＜72Hz | Fx≥72Hz |
| T4＜25℃ | 50±10 | 55±10 | 60±10 | 65±10 |
| 25℃≤T4＜30℃ | 55±10 | 60±10 | 65±10 | 70±10 |
| 30℃≤T4＜35℃ | 60±10 | 65±10 | 70±10 | 75±10 |
| 35℃≤T4＜40℃ | 65±10 | 70±10 | 75±10 | 80±10 |
| 40℃≤T4＜46℃ | 70±10 | 75±10 | 80±10 | 85±10 |
| T4≥46℃ | 70±10 | 75±10 | 80±10 | 85±10 |
| Note: T4: ambient temperature Fx: compressor frequency |  |  |  |  |

| Discharge pressure(P1) for heating/DHW mode |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Tw_out(℃) | 25 | 30 | 35 | 40 | 45 | 50 |
| P1（kPa） | 1000±100 | 1150±100 | 1300±100 | 1450±100 | 1600±100 | 1800±100 |
| Tw_out(℃) | 55 | 60 | 65 | 70 | 75 |  |
| P1（kPa） | 2000±150 | 2200±150 | 2450±150 | 2700±150 | 3000±150 |  |
| Note: P1 is absolute pressure. |  |  |  |  |  |  |

| Suction pressure(P2) for cooling mode |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Tw_out(℃) | 5～7 | 8～10 | 11～13 | 14～16 | 17～19 | 20～22 | 23～25 |
| P2（kPa） | 520±50 | 570±50 | 610±50 | 670±50 | 740±50 | 780±50 | 830±50 |
| Note: P2 is absolute pressure. |  |  |  |  |  |  |  |

Appendix to Part 4

Temperature Sensor Resistance Characteristics

| Applied to |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| T3 Outdoor unit heat exchanger bottom temperature sensor T4 Ambient temperature sensor Th Return-air temperature sensor T2 Plate heat exchanger outlet refrigerant temperature sensor T2B Plate heat exchanger inlet refrigerant temperature sensor TL Outdoor unit heat exchanger outlet temperature sensor T9i Economizer inlet temperature sensor T9o Economizer outlet temperature sensor |  |  |  |  |  |  |  |
| R25℃=10KΩ±3%，B25/50=4100K±3% |  |  |  |  |  |  |  |
| Temp. (°C) | Resistance (kΩ) |  |  | Temp. (°C) | Resistance (kΩ) |  |  |
|  | Rmax | R（t）Normal | Rmin |  | Rmax | R（t）Normal | Rmin |
| -40 | 433.108 | 383.315 | 336.854 | -8 | 57.649 | 53.458 | 49.492 |
| -39 | 404.038 | 358.094 | 315.212 | -7 | 54.456 | 50.575 | 46.899 |
| -38 | 377.08 | 334.677 | 295.088 | -6 | 51.456 | 47.862 | 44.455 |
| -37 | 352.071 | 312.924 | 276.365 | -5 | 48.636 | 45.308 | 42.15 |
| -36 | 328.859 | 292.709 | 258.939 | -4 | 45.984 | 42.903 | 39.977 |
| -35 | 307.306 | 273.916 | 242.714 | -3 | 43.49 | 40.638 | 37.927 |
| -34 | 287.285 | 256.435 | 227.599 | -2 | 41.144 | 38.504 | 35.992 |
| -33 | 268.678 | 240.17 | 213.514 | -1 | 38.935 | 36.492 | 34.165 |
| -32 | 251.38 | 225.029 | 200.382 | 0 | 36.857 | 34.596 | 32.44 |
| -31 | 235.291 | 210.929 | 188.133 | 1 | 34.898 | 32.807 | 30.81 |
| -30 | 220.32 | 197.792 | 176.705 | 2 | 33.055 | 31.12 | 29.271 |
| -29 | 206.384 | 185.547 | 166.037 | 3 | 31.317 | 29.528 | 27.815 |
| -28 | 193.407 | 174.131 | 156.075 | 4 | 29.681 | 28.026 | 26.44 |
| -27 | 181.317 | 163.481 | 146.768 | 5 | 28.138 | 26.608 | 25.14 |
| -26 | 170.049 | 153.543 | 138.071 | 6 | 26.682 | 25.268 | 23.909 |
| -25 | 159.543 | 144.266 | 129.939 | 7 | 25.31 | 24.003 | 22.745 |
| -24 | 149.745 | 135.601 | 122.333 | 8 | 24.016 | 22.808 | 21.644 |
| -23 | 140.602 | 127.507 | 115.216 | 9 | 22.794 | 21.678 | 20.601 |
| -22 | 132.067 | 119.941 | 108.555 | 10 | 21.641 | 20.61 | 19.614 |
| -21 | 124.098 | 112.867 | 102.318 | 11 | 20.553 | 19.601 | 18.68 |
| -20 | 116.539 | 106.732 | 96.92 | 12 | 19.525 | 18.646 | 17.794 |
| -19 | 110.231 | 100.552 | 91.451 | 13 | 18.554 | 17.743 | 16.955 |
| -18 | 103.743 | 94.769 | 86.328 | 14 | 17.636 | 16.888 | 16.16 |
| -17 | 97.673 | 89.353 | 81.525 | 15 | 16.769 | 16.079 | 15.406 |
| -16 | 91.99 | 84.278 | 77.017 | 16 | 15.949 | 15.313 | 14.691 |
| -15 | 86.669 | 79.521 | 72.788 | 17 | 15.174 | 14.588 | 14.014 |
| -14 | 81.684 | 75.059 | 68.815 | 18 | 14.442 | 13.902 | 13.372 |
| -13 | 77.013 | 70.873 | 65.083 | 19 | 13.748 | 13.251 | 12.762 |
| -12 | 72.632 | 66.943 | 61.574 | 20 | 13.093 | 12.635 | 12.183 |
| -11 | 68.523 | 63.252 | 58.274 | 21 | 12.471 | 12.05 | 11.634 |
| -10 | 64.668 | 59.784 | 55.169 | 22 | 11.883 | 11.496 | 11.112 |
| -9 | 61.048 | 56.524 | 52.246 | 23 | 11.327 | 10.971 | 10.617 |
| Continue on next page… |  |  |  |  |  |  |  |

| Temp. (°C) | Resistance (kΩ) |  |  | Temp. (°C) | Resistance (kΩ) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Rmax | R（t）Normal | Rmin |  | Rmax | R（t）Normal | Rmin |
| 24 | 10.8 | 10.473 | 10.147 | 65 | 2.077 | 1.953 | 1.833 |
| 25 | 10.3 | 10 | 9.7 | 66 | 2.004 | 1.883 | 1.766 |
| 26 | 9.848 | 9.551 | 9.255 | 67 | 1.934 | 1.816 | 1.702 |
| 27 | 9.418 | 9.125 | 8.834 | 68 | 1.867 | 1.752 | 1.641 |
| 28 | 9.01 | 8.721 | 8.434 | 69 | 1.802 | 1.69 | 1.582 |
| 29 | 8.621 | 8.337 | 8.055 | 70 | 1.74 | 1.631 | 1.525 |
| 30 | 8.252 | 7.972 | 7.695 | 71 | 1.68 | 1.574 | 1.471 |
| 31 | 7.9 | 7.625 | 7.353 | 72 | 1.622 | 1.519 | 1.419 |
| 32 | 7.566 | 7.296 | 7.029 | 73 | 1.567 | 1.466 | 1.369 |
| 33 | 7.247 | 6.982 | 6.721 | 74 | 1.514 | 1.416 | 1.321 |
| 34 | 6.944 | 6.684 | 6.428 | 75 | 1.463 | 1.367 | 1.275 |
| 35 | 6.656 | 6.401 | 6.15 | 76 | 1.414 | 1.321 | 1.23 |
| 36 | 6.381 | 6.131 | 5.886 | 77 | 1.367 | 1.276 | 1.188 |
| 37 | 6.119 | 5.874 | 5.634 | 78 | 1.321 | 1.233 | 1.147 |
| 38 | 5.87 | 5.63 | 5.395 | 79 | 1.277 | 1.191 | 1.108 |
| 39 | 5.631 | 5.397 | 5.167 | 80 | 1.235 | 1.151 | 1.07 |
| 40 | 5.404 | 5.175 | 4.951 | 81 | 1.195 | 1.113 | 1.034 |
| 41 | 5.188 | 4.964 | 4.745 | 82 | 1.156 | 1.076 | 0.999 |
| 42 | 4.982 | 4.763 | 4.549 | 83 | 1.118 | 1.041 | 0.966 |
| 43 | 4.785 | 4.571 | 4.362 | 84 | 1.082 | 1.007 | 0.934 |
| 44 | 4.596 | 4.387 | 4.183 | 85 | 1.047 | 0.974 | 0.903 |
| 45 | 4.417 | 4.213 | 4.014 | 86 | 1.014 | 0.942 | 0.874 |
| 46 | 4.246 | 4.046 | 3.851 | 87 | 0.982 | 0.912 | 0.845 |
| 47 | 4.082 | 3.887 | 3.697 | 88 | 0.951 | 0.883 | 0.818 |
| 48 | 3.925 | 3.735 | 3.55 | 89 | 0.921 | 0.855 | 0.791 |
| 49 | 3.776 | 3.59 | 3.409 | 90 | 0.892 | 0.828 | 0.766 |
| 50 | 3.632 | 3.451 | 3.274 | 91 | 0.864 | 0.802 | 0.742 |
| 51 | 3.495 | 3.318 | 3.146 | 92 | 0.838 | 0.777 | 0.719 |
| 52 | 3.363 | 3.191 | 3.023 | 93 | 0.812 | 0.753 | 0.696 |
| 53 | 3.237 | 3.069 | 2.905 | 94 | 0.787 | 0.73 | 0.675 |
| 54 | 3.116 | 2.952 | 2.793 | 95 | 0.763 | 0.708 | 0.654 |
| 55 | 3.001 | 2.841 | 2.685 | 96 | 0.74 | 0.686 | 0.634 |
| 56 | 2.89 | 2.734 | 2.582 | 97 | 0.718 | 0.666 | 0.615 |
| 57 | 2.784 | 2.632 | 2.484 | 98 | 0.697 | 0.646 | 0.597 |
| 58 | 2.682 | 2.534 | 2.39 | 99 | 0.677 | 0.627 | 0.579 |
| 59 | 2.585 | 2.44 | 2.299 | 100 | 0.657 | 0.609 | 0.562 |
| 60 | 2.491 | 2.35 | 2.213 | 101 | 0.638 | 0.591 | 0.546 |
| 61 | 2.401 | 2.264 | 2.13 | 102 | 0.62 | 0.574 | 0.53 |
| 62 | 2.315 | 2.181 | 2.051 | 103 | 0.602 | 0.558 | 0.515 |
| 63 | 2.233 | 2.102 | 1.975 | 104 | 0.585 | 0.542 | 0.501 |
| 64 | 2.154 | 2.026 | 1.903 | 105 | 0.569 | 0.527 | 0.485 |
| End |  |  |  |  |  |  |  |

| Applied to Tp Discharge temperature sensor |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| R90℃=5KΩ±3%，B25/50=3950K±3% |  |  |  |  |  |  |  |
| Temp. (°C) | Resistance (kΩ) |  |  | Temp. (°C) | Resistance (kΩ) |  |  |
|  | Rmax | R（t）Normal | Rmin |  | Rmax | R（t）Normal | Rmin |
| -40 | 2002.628 | 1642.059 | 1281.49 | -8 | 318.604 | 271.634 | 224.664 |
| -39 | 1881.964 | 1544.968 | 1207.972 | -7 | 302.08 | 257.867 | 213.653 |
| -38 | 1769.292 | 1454.213 | 1139.134 | -6 | 286.483 | 244.857 | 203.232 |
| -37 | 1664.009 | 1369.32 | 1074.631 | -5 | 271.757 | 232.561 | 193.365 |
| -36 | 1565.57 | 1289.862 | 1014.154 | -4 | 257.852 | 220.937 | 184.022 |
| -35 | 1473.481 | 1215.451 | 957.421 | -3 | 244.717 | 209.945 | 175.173 |
| -34 | 1387.282 | 1145.725 | 904.168 | -2 | 232.309 | 199.55 | 166.79 |
| -33 | 1306.554 | 1080.355 | 854.156 | -1 | 220.585 | 189.716 | 158.848 |
| -32 | 1230.918 | 1019.042 | 807.166 | 0 | 209.504 | 180.412 | 151.321 |
| -31 | 1160.015 | 961.505 | 762.994 | 1 | 199.029 | 171.607 | 144.186 |
| -30 | 1093.521 | 907.487 | 721.452 | 2 | 189.125 | 163.273 | 137.422 |
| -29 | 1031.137 | 856.752 | 682.368 | 3 | 179.759 | 155.383 | 131.007 |
| -28 | 972.588 | 809.086 | 645.583 | 4 | 170.899 | 147.911 | 124.923 |
| -27 | 917.615 | 764.281 | 610.947 | 5 | 162.517 | 140.835 | 119.152 |
| -26 | 865.981 | 722.152 | 578.323 | 6 | 154.585 | 134.13 | 113.675 |
| -25 | 817.469 | 682.528 | 547.586 | 7 | 147.077 | 127.778 | 108.478 |
| -24 | 771.875 | 645.245 | 518.616 | 8 | 139.97 | 121.757 | 103.544 |
| -23 | 729.009 | 610.156 | 491.303 | 9 | 133.239 | 116.049 | 98.859 |
| -22 | 688.698 | 577.121 | 465.544 | 10 | 126.864 | 110.638 | 94.411 |
| -21 | 650.778 | 546.012 | 441.246 | 11 | 120.825 | 105.505 | 90.185 |
| -20 | 615.097 | 516.708 | 418.318 | 12 | 115.103 | 100.636 | 86.17 |
| -19 | 581.515 | 489.096 | 396.678 | 13 | 109.679 | 96.017 | 82.354 |
| -18 | 549.899 | 463.073 | 376.247 | 14 | 104.537 | 91.633 | 78.728 |
| -17 | 520.129 | 438.542 | 356.955 | 15 | 99.662 | 87.471 | 75.28 |
| -16 | 492.089 | 415.411 | 338.733 | 16 | 95.038 | 83.52 | 72.001 |
| -15 | 465.672 | 393.595 | 321.518 | 17 | 90.652 | 79.767 | 68.882 |
| -14 | 440.779 | 373.014 | 305.25 | 18 | 86.489 | 76.202 | 65.915 |
| -13 | 417.316 | 353.595 | 289.874 | 19 | 82.539 | 72.815 | 63.091 |
| -12 | 395.197 | 335.268 | 275.339 | 20 | 78.789 | 69.596 | 60.404 |
| -11 | 374.34 | 317.967 | 261.594 | 21 | 75.228 | 66.537 | 57.845 |
| -10 | 354.669 | 301.632 | 248.595 | 22 | 71.846 | 63.627 | 55.409 |
| -9 | 336.113 | 286.206 | 236.298 | 23 | 68.633 | 60.86 | 53.088 |
| Continue on next page… |  |  |  |  |  |  |  |

| Temp. (°C) | Resistance (kΩ) |  |  | Temp. (°C) | Resistance (kΩ) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Rmax | R（t）Normal | Rmin |  | Rmax | R（t）Normal | Rmin |
| 24 | 65.58 | 58.228 | 50.877 | 66 | 11.858 | 11.134 | 10.411 |
| 25 | 62.678 | 55.724 | 48.77 | 67 | 11.432 | 10.749 | 10.066 |
| 26 | 59.919 | 53.34 | 46.762 | 68 | 11.024 | 10.38 | 9.735 |
| 27 | 57.295 | 51.071 | 44.847 | 69 | 10.632 | 10.024 | 9.416 |
| 28 | 54.8 | 48.91 | 43.021 | 70 | 10.255 | 9.682 | 9.109 |
| 29 | 52.426 | 46.853 | 41.279 | 71 | 9.894 | 9.354 | 8.814 |
| 30 | 50.167 | 44.892 | 39.617 | 72 | 9.546 | 9.038 | 8.53 |
| 31 | 48.016 | 43.024 | 38.031 | 73 | 9.213 | 8.734 | 8.255 |
| 32 | 45.969 | 41.243 | 36.517 | 74 | 8.892 | 8.442 | 7.992 |
| 33 | 44.019 | 39.546 | 35.072 | 75 | 8.584 | 8.161 | 7.737 |
| 34 | 42.162 | 37.927 | 33.692 | 76 | 8.288 | 7.89 | 7.492 |
| 35 | 40.392 | 36.383 | 32.373 | 77 | 8.003 | 7.629 | 7.256 |
| 36 | 38.706 | 34.91 | 31.113 | 78 | 7.729 | 7.379 | 7.028 |
| 37 | 37.098 | 33.504 | 29.909 | 79 | 7.466 | 7.137 | 6.809 |
| 38 | 35.566 | 32.162 | 28.758 | 80 | 7.213 | 6.905 | 6.597 |
| 39 | 34.104 | 30.881 | 27.657 | 81 | 6.969 | 6.681 | 6.393 |
| 40 | 32.709 | 29.657 | 26.605 | 82 | 6.735 | 6.466 | 6.196 |
| 41 | 31.379 | 28.488 | 25.598 | 83 | 6.509 | 6.258 | 6.006 |
| 42 | 30.109 | 27.372 | 24.634 | 84 | 6.292 | 6.058 | 5.823 |
| 43 | 28.896 | 26.304 | 23.712 | 85 | 6.084 | 5.865 | 5.646 |
| 44 | 27.739 | 25.284 | 22.829 | 86 | 5.883 | 5.679 | 5.476 |
| 45 | 26.633 | 24.309 | 21.984 | 87 | 5.689 | 5.5 | 5.311 |
| 46 | 25.577 | 23.376 | 21.174 | 88 | 5.502 | 5.327 | 5.152 |
| 47 | 24.568 | 22.483 | 20.399 | 89 | 5.323 | 5.161 | 4.998 |
| 48 | 23.603 | 21.629 | 19.656 | 90 | 5.15 | 5 | 4.85 |
| 49 | 22.681 | 20.812 | 18.943 | 91 | 4.996 | 4.845 | 4.694 |
| 50 | 21.799 | 20.03 | 18.261 | 92 | 4.847 | 4.696 | 4.545 |
| 51 | 20.956 | 19.281 | 17.606 | 93 | 4.703 | 4.552 | 4.4 |
| 52 | 20.149 | 18.563 | 16.978 | 94 | 4.564 | 4.412 | 4.261 |
| 53 | 19.377 | 17.876 | 16.375 | 95 | 4.43 | 4.278 | 4.127 |
| 54 | 18.638 | 17.218 | 15.797 | 96 | 4.3 | 4.149 | 3.997 |
| 55 | 17.931 | 16.587 | 15.243 | 97 | 4.175 | 4.024 | 3.872 |
| 56 | 17.254 | 15.982 | 14.71 | 98 | 4.054 | 3.903 | 3.752 |
| 57 | 16.606 | 15.402 | 14.199 | 99 | 3.937 | 3.787 | 3.636 |
| 58 | 15.984 | 14.846 | 13.708 | 100 | 3.824 | 3.674 | 3.524 |
| 59 | 15.389 | 14.313 | 13.236 | 101 | 3.715 | 3.565 | 3.416 |
| 60 | 14.819 | 13.801 | 12.783 | 102 | 3.609 | 3.46 | 3.312 |
| 61 | 14.272 | 13.31 | 12.348 | 103 | 3.507 | 3.359 | 3.211 |
| 62 | 13.748 | 12.839 | 11.929 | 104 | 3.409 | 3.261 | 3.114 |
| 63 | 13.246 | 12.387 | 11.527 | 105 | 3.313 | 3.167 | 3.02 |
| 64 | 12.764 | 11.952 | 11.14 | 106 | 3.221 | 3.075 | 2.929 |
| 65 | 12.302 | 11.535 | 10.768 | 107 | 3.131 | 2.987 | 2.842 |
| Continue on next page… |  |  |  |  |  |  |  |

| Temp. (°C) | Resistance (kΩ) |  |  | Temp. (°C) | Resistance (kΩ) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Rmax | R（t）Normal | Rmin |  | Rmax | R（t）Normal | Rmin |
| 108 | 3.045 | 2.901 | 2.758 | 130 | 1.707 | 1.59 | 1.473 |
| 109 | 2.962 | 2.819 | 2.676 | 131 | 1.665 | 1.55 | 1.434 |
| 110 | 2.881 | 2.739 | 2.597 | 132 | 1.625 | 1.511 | 1.397 |
| 111 | 2.802 | 2.662 | 2.521 | 133 | 1.586 | 1.473 | 1.36 |
| 112 | 2.727 | 2.587 | 2.448 | 134 | 1.548 | 1.436 | 1.324 |
| 113 | 2.653 | 2.515 | 2.377 | 135 | 1.511 | 1.401 | 1.29 |
| 114 | 2.582 | 2.445 | 2.308 | 136 | 1.475 | 1.366 | 1.257 |
| 115 | 2.514 | 2.378 | 2.242 | 137 | 1.44 | 1.332 | 1.225 |
| 116 | 2.447 | 2.313 | 2.178 | 138 | 1.407 | 1.3 | 1.193 |
| 117 | 2.383 | 2.249 | 2.116 | 139 | 1.374 | 1.268 | 1.163 |
| 118 | 2.32 | 2.188 | 2.056 | 140 | 1.342 | 1.238 | 1.133 |
| 119 | 2.26 | 2.129 | 1.998 | 141 | 1.311 | 1.208 | 1.105 |
| 120 | 2.201 | 2.072 | 1.942 | 142 | 1.281 | 1.179 | 1.077 |
| 121 | 2.145 | 2.016 | 1.888 | 143 | 1.252 | 1.151 | 1.051 |
| 122 | 2.09 | 1.963 | 1.836 | 144 | 1.224 | 1.124 | 1.024 |
| 123 | 2.037 | 1.911 | 1.785 | 145 | 1.196 | 1.098 | 0.999 |
| 124 | 1.985 | 1.86 | 1.736 | 146 | 1.169 | 1.072 | 0.975 |
| 125 | 1.935 | 1.812 | 1.689 | 147 | 1.143 | 1.047 | 0.951 |
| 126 | 1.887 | 1.765 | 1.643 | 148 | 1.118 | 1.023 | 0.928 |
| 127 | 1.84 | 1.719 | 1.598 | 149 | 1.093 | 0.999 | 0.905 |
| 128 | 1.794 | 1.675 | 1.555 | 150 | 1.069 | 0.977 | 0.884 |
| 129 | 1.75 | 1.632 | 1.514 | / | / | / | / |
| End |  |  |  |  |  |  |  |

| Applied to TW_in Plate heat exchanger inlet water temperature sensor TW_out Plate heat exchanger outlet water temperature sensor T5 Water tank temperature sensor TW2 Zone 2 water flow temperature sensor |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| R50℃=17.6KΩ±3%，B0/100=3970K±2% |  |  |  |  |  |  |  |
| Temp. (°C) | Resistance (kΩ) |  |  | Temp. (°C) | Resistance (kΩ) |  |  |
|  | Rmax | R（t）Normal | Rmin |  | Rmax | R（t）Normal | Rmin |
| -40 | 1822.916 | 1608.351 | 1393.786 | -8 | 263.273 | 242.131 | 220.989 |
| -39 | 1705.939 | 1507.271 | 1308.602 | -7 | 249.357 | 229.593 | 209.828 |
| -38 | 1596.976 | 1412.994 | 1229.013 | -6 | 236.255 | 217.774 | 199.293 |
| -37 | 1495.47 | 1325.058 | 1154.647 | -5 | 223.915 | 206.63 | 189.345 |
| -36 | 1400.897 | 1243.025 | 1085.152 | -4 | 212.289 | 196.119 | 179.949 |
| -35 | 1312.771 | 1166.486 | 1020.2 | -3 | 201.332 | 186.201 | 171.07 |
| -34 | 1230.637 | 1095.061 | 959.485 | -2 | 191.001 | 176.84 | 162.678 |
| -33 | 1154.07 | 1028.393 | 902.717 | -1 | 181.258 | 168.001 | 154.744 |
| -32 | 1082.675 | 966.151 | 849.626 | 0 | 172.066 | 159.653 | 147.24 |
| -31 | 1016.084 | 908.023 | 799.962 | 1 | 163.391 | 151.766 | 140.141 |
| -30 | 953.957 | 853.724 | 753.491 | 2 | 155.2 | 144.311 | 133.422 |
| -29 | 896.053 | 802.986 | 709.918 | 3 | 147.466 | 137.264 | 127.062 |
| -28 | 842.002 | 755.557 | 669.113 | 4 | 140.159 | 130.599 | 121.038 |
| -27 | 791.53 | 711.21 | 630.889 | 5 | 133.253 | 124.293 | 115.332 |
| -26 | 744.384 | 669.728 | 595.072 | 6 | 126.725 | 118.326 | 109.926 |
| -25 | 700.328 | 630.913 | 561.498 | 7 | 120.554 | 112.679 | 104.803 |
| -24 | 659.144 | 594.58 | 530.015 | 8 | 114.715 | 107.33 | 99.945 |
| -23 | 620.629 | 560.556 | 500.483 | 9 | 109.191 | 102.265 | 95.338 |
| -22 | 584.595 | 528.683 | 472.771 | 10 | 103.963 | 97.466 | 90.969 |
| -21 | 550.871 | 498.814 | 446.757 | 11 | 99.013 | 92.918 | 86.822 |
| -20 | 519.295 | 470.812 | 422.328 | 12 | 94.327 | 88.607 | 82.888 |
| -19 | 489.718 | 444.548 | 399.379 | 13 | 89.887 | 84.519 | 79.152 |
| -18 | 462.003 | 419.907 | 377.812 | 14 | 85.679 | 80.642 | 75.604 |
| -17 | 436.022 | 396.779 | 357.537 | 15 | 81.692 | 76.963 | 72.234 |
| -16 | 411.657 | 375.063 | 338.468 | 16 | 77.911 | 73.471 | 69.032 |
| -15 | 388.797 | 354.662 | 320.527 | 17 | 74.326 | 70.157 | 65.989 |
| -14 | 367.343 | 335.492 | 303.641 | 18 | 70.925 | 67.011 | 63.097 |
| -13 | 347.198 | 317.47 | 287.743 | 19 | 67.699 | 64.023 | 60.347 |
| -12 | 328.275 | 300.521 | 272.767 | 20 | 64.636 | 61.184 | 57.731 |
| -11 | 310.495 | 284.576 | 258.658 | 21 | 61.729 | 58.486 | 55.243 |
| -10 | 293.78 | 269.569 | 245.359 | 22 | 58.967 | 55.921 | 52.875 |
| -9 | 278.06 | 255.439 | 232.818 | 23 | 56.345 | 53.483 | 50.621 |
| Continue on next page… |  |  |  |  |  |  |  |

| Temp. (°C) | Resistance (kΩ) |  |  | Temp. (°C) | Resistance (kΩ) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Rmax | R（t）Normal | Rmin |  | Rmax | R（t）Normal | Rmin |
| 24 | 53.854 | 51.165 | 48.476 | 66 | 10.231 | 9.818 | 9.405 |
| 25 | 51.485 | 48.959 | 46.432 | 67 | 9.887 | 9.481 | 9.075 |
| 26 | 49.234 | 46.86 | 44.486 | 68 | 9.556 | 9.157 | 8.758 |
| 27 | 47.094 | 44.863 | 42.632 | 69 | 9.237 | 8.846 | 8.454 |
| 28 | 45.058 | 42.961 | 40.865 | 70 | 8.932 | 8.547 | 8.163 |
| 29 | 43.121 | 41.151 | 39.181 | 71 | 8.637 | 8.259 | 7.882 |
| 30 | 41.278 | 39.427 | 37.575 | 72 | 8.354 | 7.983 | 7.613 |
| 31 | 39.524 | 37.784 | 36.044 | 73 | 8.08 | 7.717 | 7.354 |
| 32 | 37.854 | 36.219 | 34.583 | 74 | 7.818 | 7.461 | 7.105 |
| 33 | 36.263 | 34.726 | 33.189 | 75 | 7.565 | 7.215 | 6.866 |
| 34 | 34.748 | 33.304 | 31.86 | 76 | 7.322 | 6.978 | 6.635 |
| 35 | 33.305 | 31.947 | 30.59 | 77 | 7.087 | 6.75 | 6.414 |
| 36 | 31.929 | 30.653 | 29.378 | 78 | 6.861 | 6.531 | 6.201 |
| 37 | 30.617 | 29.419 | 28.22 | 79 | 6.643 | 6.319 | 5.995 |
| 38 | 29.367 | 28.241 | 27.114 | 80 | 6.433 | 6.115 | 5.798 |
| 39 | 28.174 | 27.115 | 26.057 | 81 | 6.23 | 5.919 | 5.608 |
| 40 | 27.036 | 26.042 | 25.048 | 82 | 6.035 | 5.73 | 5.425 |
| 41 | 25.949 | 25.015 | 24.082 | 83 | 5.847 | 5.548 | 5.249 |
| 42 | 24.913 | 24.036 | 23.159 | 84 | 5.666 | 5.372 | 5.079 |
| 43 | 23.924 | 23.1 | 22.276 | 85 | 5.491 | 5.204 | 4.916 |
| 44 | 22.979 | 22.206 | 21.432 | 86 | 5.323 | 5.041 | 4.759 |
| 45 | 22.076 | 21.35 | 20.624 | 87 | 5.16 | 4.884 | 4.608 |
| 46 | 21.213 | 20.532 | 19.85 | 88 | 5.003 | 4.732 | 4.462 |
| 47 | 20.389 | 19.749 | 19.11 | 89 | 4.852 | 4.587 | 4.322 |
| 48 | 19.602 | 19.001 | 18.401 | 90 | 4.706 | 4.446 | 4.186 |
| 49 | 18.848 | 18.285 | 17.722 | 91 | 4.565 | 4.31 | 4.056 |
| 50 | 18.128 | 17.6 | 17.072 | 92 | 4.429 | 4.179 | 3.929 |
| 51 | 17.466 | 16.944 | 16.422 | 93 | 4.298 | 4.053 | 3.809 |
| 52 | 16.831 | 16.316 | 15.801 | 94 | 4.172 | 3.932 | 3.692 |
| 53 | 16.223 | 15.714 | 15.206 | 95 | 4.049 | 3.814 | 3.579 |
| 54 | 15.641 | 15.139 | 14.638 | 96 | 3.932 | 3.701 | 3.471 |
| 55 | 15.081 | 14.586 | 14.092 | 97 | 3.817 | 3.591 | 3.365 |
| 56 | 14.545 | 14.058 | 13.571 | 98 | 3.708 | 3.486 | 3.265 |
| 57 | 14.03 | 13.55 | 13.07 | 99 | 3.601 | 3.384 | 3.167 |
| 58 | 13.537 | 13.064 | 12.591 | 100 | 3.499 | 3.286 | 3.073 |
| 59 | 13.063 | 12.597 | 12.132 | 101 | 3.4 | 3.191 | 2.983 |
| 60 | 12.608 | 12.15 | 11.692 | 102 | 3.303 | 3.098 | 2.894 |
| 61 | 12.171 | 11.721 | 11.27 | 103 | 3.21 | 3.009 | 2.809 |
| 62 | 11.752 | 11.309 | 10.866 | 104 | 3.12 | 2.923 | 2.727 |
| 63 | 11.349 | 10.913 | 10.478 | 105 | 3.032 | 2.84 | 2.647 |
| 64 | 10.962 | 10.533 | 10.105 | 106 | 2.948 | 2.759 | 2.571 |
| 65 | 10.589 | 10.168 | 9.748 | 107 | 2.866 | 2.681 | 2.497 |
| Continue on next page… |  |  |  |  |  |  |  |

| Temp. (°C) | Resistance (kΩ) |  |  | Temp. (°C) | Resistance (kΩ) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Rmax | R（t）Normal | Rmin |  | Rmax | R（t）Normal | Rmin |
| 108 | 2.787 | 2.606 | 2.425 | 130 | 1.553 | 1.436 | 1.318 |
| 109 | 2.711 | 2.533 | 2.356 | 131 | 1.515 | 1.399 | 1.284 |
| 110 | 2.637 | 2.463 | 2.288 | 132 | 1.477 | 1.364 | 1.251 |
| 111 | 2.565 | 2.394 | 2.224 | 133 | 1.44 | 1.329 | 1.219 |
| 112 | 2.496 | 2.328 | 2.161 | 134 | 1.405 | 1.296 | 1.187 |
| 113 | 2.428 | 2.264 | 2.1 | 135 | 1.37 | 1.264 | 1.157 |
| 114 | 2.363 | 2.202 | 2.041 | 136 | 1.337 | 1.232 | 1.127 |
| 115 | 2.3 | 2.142 | 1.985 | 137 | 1.304 | 1.202 | 1.099 |
| 116 | 2.239 | 2.084 | 1.93 | 138 | 1.273 | 1.172 | 1.071 |
| 117 | 2.179 | 2.028 | 1.876 | 139 | 1.242 | 1.143 | 1.044 |
| 118 | 2.122 | 1.973 | 1.825 | 140 | 1.212 | 1.115 | 1.018 |
| 119 | 2.066 | 1.92 | 1.775 | 141 | 1.183 | 1.088 | 0.993 |
| 120 | 2.012 | 1.869 | 1.726 | 142 | 1.155 | 1.061 | 0.968 |
| 121 | 1.96 | 1.82 | 1.68 | 143 | 1.127 | 1.036 | 0.944 |
| 122 | 1.909 | 1.772 | 1.634 | 144 | 1.101 | 1.011 | 0.921 |
| 123 | 1.86 | 1.725 | 1.59 | 145 | 1.075 | 0.986 | 0.898 |
| 124 | 1.812 | 1.68 | 1.548 | 146 | 1.05 | 0.963 | 0.876 |
| 125 | 1.765 | 1.636 | 1.506 | 147 | 1.025 | 0.94 | 0.855 |
| 126 | 1.72 | 1.593 | 1.466 | 148 | 1.001 | 0.918 | 0.834 |
| 127 | 1.677 | 1.552 | 1.428 | 149 | 0.978 | 0.896 | 0.814 |
| 128 | 1.634 | 1.512 | 1.39 | 150 | 0.955 | 0.875 | 0.794 |
| 129 | 1.593 | 1.473 | 1.354 | / | / | / | / |
| End |  |  |  |  |  |  |  |

Pressure and Output voltage characteristics of Pressure sensor

Output voltage formula of high-pressure sensor：Vout(H)=0.87×PH+0.5

Output voltage formula of low-pressure sensor：Vout(L)=2×PL+0.5

Main Control

PCB

Pressure sensor

Vcc

Vout

GND

Measure the DC Voltage

Measure the output voltage of pressure sensor

Guide for identifying Compressor & Fan Inverter PCB or Fan Inverter PCB failure

Before measuring the Compressor & Fan Inverter PCB or Fan Inverter PCB, please confirm steps below in advance:

1) Cut off the power supply.

2) Wait for 10 min for capacitor discharging in order to avoid the electric shock.

3) Remove all connections wires.

4) To identify whether Compressor & Fan Inverter PCB failed, follow the guide to test inverter circuit and three phase bridge rectifier. If any one of test value abnormal, the Compressor & Fan Inverter PCB failed.

5) To identify whether Fan Inverter PCB failed, follow the guide to test inverter circuit rectifier. If any one of test value abnormal, the Fan Inverter PCB failed.

Preparing tools: multimeter (secondary tube is available)

Select

Compressor & Fan Inverter PCB

Inverter circuit (Fan module/ Compressor module):

| Order | Test point |  | Normal | Abnormal |
| --- | --- | --- | --- | --- |
|  | +(Red) | -（Black） |  |  |
| 1 | U | P-in | 0.3 V-0.7 V | 0 / Infinite |
| 2 | V | P-in |  |  |
| 3 | W | P-in |  |  |
| 4 | N | U |  |  |
| 5 | N | V |  |  |
| 6 | N | W |  |  |
| Note: 1. If any one of test value abnormal, the Compressor & Fan Inverter PCB failed. Request aftersales service and replace the Compressor & Fan Inverter PCB. |  |  |  |  |

Compressor & Fan Inverter PCB

Three phase bridge rectifier:

| Order | Test point |  | Normal | Abnormal |
| --- | --- | --- | --- | --- |
|  | +(Red) | -（Black） |  |  |
| 1 | L1 | P-out | 0.3 V -0.7 V | 0 / Infinite |
| 2 | L2 | P-out |  |  |
| 3 | L3 | P-out |  |  |
| 4 | N | L1 |  |  |
| 5 | N | L2 |  |  |
| 6 | N | L3 |  |  |
| Note: 1. If any one of test value abnormal, the Compressor & Fan Inverter PCB failed. Request aftersales service and replace the Compressor & Fan Inverter PCB. |  |  |  |  |

Fan Inverter PCB

Inverter circuit (The second Fan module):

| Order | Test point |  | Normal | Abnormal |
| --- | --- | --- | --- | --- |
|  | +(Red) | -（Black） |  |  |
| 1 | U | P | 0.3 V -0.7 V | 0 / Infinite |
| 2 | V | P |  |  |
| 3 | W | P |  |  |
| 4 | N | U |  |  |
| 5 | N | V |  |  |
| 6 | N | W |  |  |
| Note: 1. If any one of test value abnormal, the Fan Inverter PCB failed. Request aftersales service and replace the Fan Inverter PCB. |  |  |  |  |

Fan Inverter PCB